v0.2.0-alpha

March 2025

Interior Epoxy Coating vs Bare Pipe: Comparative Analysis  
of Corrosion Mitigation Strategies in Water Pipelines[[1]](#footnote-1)

I.Mella[[2]](#footnote-2)

*Abstract*— This white paper presents a lifecycle cost analysis of two corrosion mitigation strategies for water pipeline systems: corrosion allowance through increased wall thickness and the application of interior epoxy coatings. The study evaluates the economic and operational performance of both approaches over a 25-year service life, considering capital expenditures (CAPEX), operational expenditures (OPEX).

# Introduction

The strategic selection of corrosion mitigation approaches significantly impacts both operational longevity and lifecycle costs in water transmission infrastructure. This investigation evaluates two prevalent methodologies: corrosion allowance designs utilizing increased wall thickness versus epoxy-coated pipeline systems employing protective barriers.

Pipeline systems relying solely on wall thickness augmentation inherently reduce internal diameters, directly increasing pumping energy requirements. This hydraulic inefficiency becomes compounded by the elevated surface roughness characteristics of uncoated steel compared to epoxy-lined alternatives. Furthermore, bare steel systems necessitate continuous chemical inhibitor treatments to mitigate corrosion progression - introducing recurring material costs and operational complexities absent in coated systems.

This study conducts a techno-economic analysis encompassing both capital expenditures (CAPEX) and operational costs (OPEX) across a 25-year service horizon. The evaluation framework incorporates hydraulic modeling, material degradation rates, and chemical treatment protocols to quantify total ownership costs for both mitigation strategies.

# Background: Pipelines in Chile

High-elevation pipeline systems in Chile, particularly those located at altitudes exceeding 3,000 meters above sea level, present significant cost challenges due to their complex engineering requirements, the need for buried infrastructure, and energy-intensive pumping operations.

The average construction cost for such pipelines is approximately $3.2 million per kilometer, reflecting a 23% increase since 2018. This rise is attributed to factors such as material cost inflation, higher labor expenses, and increased energy prices. These financial pressures underscore the need for innovative financing and operational strategies to support the development of critical water infrastructure in high-altitude regions.

BOOT (Build, Own, Operate, Transfer) contracts are rapidly become a preferred model for securing water resources in the mining sector. These agreements allow mining companies to transfer project risks and reduce upfront capital expenditures by outsourcing the development, ownership, and operation of water infrastructure to specialized firms. This approach enables mining companies to focus on their core activities while ensuring long-term water security and reliable delivery.

Prominent examples of successful BOOT projects include the Centinela and Spence operations, as well as Codelco's SADDN project. These initiatives highlight the practical benefits of this model in addressing water challenges while supporting sustainable development in the mining industry.

These specialized firms are the ones in need to maximize return over their investment and minimize failure risks.

Table . Significant water pipeline projects.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ***Name*** | ***Year*** | ***Owner*** | ***Size*** | ***Length*** | ***Coatings*** | ***Water*** |
| **Monturaqui** | 1998 | MEL | 36" | 90 | FBE | well |
| **Pelambres** | 2007 | AMSA | 32 | 50 | FBE | recovered |
| **Coloso** | 2008 | MEL | 24" | 130 | LE➜Bare | desal |
| **Centinela** | 2011 | AMSA | 36" | 160 | Bare | seawater |
| **Candelaria** | 2012 | Lundin | 24” | 80 | FBE&HDPE | desal |
| **Cerro Negro** | 2013 | CAP | 24 | 90 | FBE➜HDPE | desal |
| **Mantoverde** | 2013 | Capstone | 24" | 50 | FBE | desal |
| **SGorda** | 2014 | SGSCM | 36" | 140 | Bare➜HDPE | seawater |
| **EWS** | 2014 | MEL | 2x42" | 160 | Primed FBE | desal |
| **Spence SGO** | 2018 | BHP | 36" | 160 | LE | desal |
| **EWSE** | 2019 | MEL | 2x42" | 160 | Primed FBE | desal |
| **INCO** | 2022 | AMSA | 24" | 60 | Bare | desal |
| **QBlanca** | 2023 | Teck | 36" | 160 | Bare | desal |
| **Aconcagua** | 2025 | APacifico | 28" | 120 | LE | desal |
| **PAO** | 2026 | AMSA | 28" | 60 | Primed FBE | desal |
| **C20+** | 2026 | CMDIC | 44" | 194 | FBE | desal |
| **RTomic** | 2026 | Codelco | 48" | 160 | LE | desal |
| **Capellan** | 2026 | Adasa | 28" | 24 | Bare | recovered |
| **TEA** | 2026 | SQM | 36" | 90 | FBE | seawater |
| **Cenizas** | 2027 | MCenizas | 12" | 120 | FBE | desal |

LE= Liquid Epoxy; FBE = Fusion Bonded Epoxy.

# Case study parameters and Computational Methodology

To facilitate a comparative evaluation of different corrosion mitigation strategies, the analysis employs a representative water transport scenario constructed with the following arbitrary parameters:

Table . Arbitrary Project Parameters

|  |  |  |
| --- | --- | --- |
| Parameter | Value | Unit |
| Pipeline length | 100 | km |
| Static head (elevation change) | 1000 | m |
| Pipeline outside diameter | 28 | inches |
| Design wall thickness assuming no corrosion | 9.53 | mm |
| Average corrosion rate | 0.15 | mm/yr |
| Density of water | 1030 | kg/m³ |
| Dynamic viscosity of water | 0.0013 | Pa·s |
| Roughness bare year 1 | 0.068 | mm |
| Roughness bare year 25 | 0.720 | mm |
| Roughness FBE year 1 | 0.015 | mm |
| Roughness FBE year 25 | 0.035 | mm |
| Design flow rate | 700 | L/s |
| Service life | 25 | years |
| Annual hours of operation | 8400 | h/yr |
| Pump efficiency | 82 | % |
| Annual discount Rate | 10 | % |
| Field internal joint coating service | $1,000 | $/joint |
| Electrical energy | 175 | $/MWh |
| Hot-rolled coil (HRC) Chinese spot price | 470 | $/t |
| FBE cost per interior surface area | 9.0 | $/m² |

These parameters can be modified in the Excel file included in the GitHub repository.

All computational models and datasets are [publicly accessible via GitHub](https://github.com/ignaciomella/Bare-vs-Coated-Water-Pipelines/), including an Excel workbook implementing the Newton-Raphson iterative technique for precise determination of Darcy-Weisbach friction factor.

The author expects that this methodological transparency enables independent verification of results while providing an adaptable framework for evaluating corrosion management strategies under diverse operational conditions. This systematic approach aims to advance evidence-based decision-making in pipeline engineering practices.

# Capital Expenditure Analysis

## Steel Pipe Economics

This cost model integrates current hot-rolled coil (HRC) market indices, manufacturing premiums, and logistical expenses to establish a baseline steel pipe pricing. This is because HRC is a primary raw material for steel pipe production, and its price movements closely reflect changes in the broader steel market.

Recent analysis of the Chinese steel market highlights that the production of API 5L X70 steel pipe typically incurs costs ranging between 1.6x to 2.2x the prevailing HRC spot prices. This multiplier reflects the value-added processes required to transform raw HRC into finished X70 pipe [1, 2, 3].

For this study, the following assumptions will be applied:

### Baseline hot-rolled coil (HRC) Chinese spot price

The model assumes a Chinese HRC spot price of **$****470 per tonne**, based on current market conditions [4].

### Value-added multiplier:

A conservative value-added multiplier of **1.6x** is used to estimate the manufacturing premiums cost from China Hot rolled coil Spot Price to API 5L X70 steel pipe cost.

### Transportation cost

This study uses **$170/t** transportation cost from the steel mill in China to the job site in Chile. This cost includes inland trasnportation from the mill to the Chinese port ($15/t), ocean freight ($120/t), and inland transportation between Chilean port and the job site ($35/t).

Using these parameters, the estimated cost for API 5L X70 steel pipe is calculated as follows:

X70 Cost per Weight (*CPW*) = **$470/t** × **1.6** + **$170/t** = **$922/t**

The average corrosion rate for the corrosion allowance (bare pipe) strategy it is assumed at **0.15 mm/yr** which should holds validity for industrial water systems with adequate inhibitors injection [5]. Note that the extra wall thickness considered for the corrosion allowance strategy assumes corrosion inhibitors to mitiagate the corrosion from a standard 0.22-0.32 mm/yr to the current assumed 0.15 mm/yr [6].

The wall thickness required for the coated pipe is **9.53 mm** (project design wall thickness). Adding 0.15 mm/yr × 25 yr = **3.75 mm** to this wall thickness results in **13.28 mm** of initial wall thickiness for the corrosion allowance strategy. With these values we calculate the total pipeline steel costs via hollow cylinder volumetrics:

(1)

Where ***D* = 0.7112 m** (external diameter), ***t* = 13.28 mm** (bare pipe) or **9.53 mm** (coated system), ***L* = 100 km** (pipeline length), and ***ρ* = 7850 kg/m³** (API 5L · X70 steel density).

Replacing these values in (1) we obtain the steel pipe cost for each strategy.

Table . Steel cost for each strategy

|  |  |  |  |
| --- | --- | --- | --- |
| ***Item*** | ***Bare*** | ***Coated*** | ***Corrosion Steel*** |
| Wall thickness | 13.28 mm | 9.53 mm |  |
| Steel Weight | 22,857 t | 16,491 t |  |
| Steel pipe cost | $21,074,349 | $15,204,644 | $4,583,412 |
| Extra corrosion steel represents 27.9% of the baseline steel material expenditure. | | | |

## Interior FBE Coating Economics

The process of coating the interior of a steel pipe involves two distinct steps. First, an initial coating is applied at the manufacturing facility under controlled factory conditions. Subsequently, once the pipe sections are welded together on-site, a field joint coating is applied to protect the welded joint and ensure continuity of the protective layer.

### Shop-applied interior fusion-bonded epoxy (FBE)

Shop-applied interior fusion-bonded epoxy (FBE) coatings, typically applied at thicknesses up to 500 µm, offer cost efficiencies [7]. These efficiencies stem from industrialized application processes that deliver superior resistance to chloride-induced corrosion and abrasion caused by suspended solids.

Current pricing of $6.50–$6.00/m² for surface treatment processes reflects the integration of material inputs, thermal energy requirements, and automated systems in modern pipe mills, with specific costs varying by region and coating type. This analysis adopts a **$6.00/m²** cost per interior surface area (CPS) to calculate coating expenditures [8].


(2)

Where ***D* = 0.69214 m** (coated interior diameter) and ***L* = 100 km** (pipeline length).

Replaceing this values in (2):

= $1,304,653

Implementation costs total $**1,304,653**, representing **7.9%** of the baseline steel material expenditure.

Chart 1. Shop FBE coating compared to steel cost.  


### Internal Robotic Field Joint Coating

Steel pipes with shop-applied FBE coatings typically feature uncoated ends (cutbacks) measuring approximately 50 mm. These cutbacks facilitate welding operations, prevent heat-induced damage to the existing coatings during installation, and simplify subsequent field joint recoating procedures. However, welding inevitably generates significant thermal stress, degrading the nearby FBE layers and creating heat-affected zones (HAZ). These compromised areas require careful restoration to ensure continuous corrosion protection throughout the pipeline.

To address this critical issue, internal robotic field joint coating systems have been developed. These sophisticated robotic crawlers are specifically designed to navigate pipeline interiors, applying protective epoxy coatings directly onto weld joints. The process begins by thoroughly cleaning and preparing the cutback area using abrasive blasting techniques (typically achieving SA 2.5 cleanliness). This step removes contaminants such as rust, mill scale, oils, and salts, providing an optimal surface profile for coating adhesion.



1998 Project, Minera Escondida Monturaqui, Atacama, Chile 18” – 42” Water Pipeline. 7,500 Field Joint Internally Coated with FBE

Following surface preparation, specialized epoxy formulations designed explicitly for field applications are applied using automated robotic equipment equipped with electrostatic spray nozzles. These formulations must cure rapidly under ambient conditions while delivering comparable resistance to mechanical damage, chemical exposure, and corrosion as their shop-applied counterparts. Robotic systems utilize real-time camera monitoring and precise control mechanisms to ensure uniform coating thickness and complete coverage of weld zones.

Currently, two dominant robotic coating providers serve this niche market: Aegion/CRTS and TYHOO Group. Aegion/CRTS offers premium robotic systems that are approximately 20–30% more expensive but provide superior precision, lower rework rates, and enhanced reliability—particularly beneficial for large-diameter pipelines (above 28 inches). Conversely, TYHOO Group provides budget-friendly modular robots optimized primarily for pipelines projects with tighter budget constraints.

Nevertheless, reliance on only two specialized providers introduces significant project risks related to limited market competition. This market concentration may negatively impact service availability, pricing stability, responsiveness during maintenance or repairs, and timely technical support.

Given these complexities and associated risks with robotic field joint coating applications—including high mobilization costs, logistical challenges related to remote sites, environmental sensitivity affecting coating quality (temperature fluctuations ±15°C; humidity variations between 30–95% RH), and elevated defect rates compared to shop-applied coatings—pipeline operators must carefully evaluate alternative joining technologies or invest significantly in rigorous quality control procedures.

The robotic interior coating service cost per joint varies between $800 to $1,200 per joint depending mainly on the site location, the diameter and the length of the pipeline[9]. This analysis will consider a price per joint of **$1,000 per joint**. For the 8,334-joint pipeline, this aggregates to **$8,334,000** which is **6.4 times** the cost of the Interior FBE Coating.

Table . CAPEX Composition for Coated Pipe

|  |  |  |  |
| --- | --- | --- | --- |
| CAPEX Item | Cost | % | Surface |
| Total steel cost | $15,204,644 | 61.2% |  |
| Field joint coating | **$8,334,000** | 33.5% | 0.42% |
| Shop FBE coating | $1,304,653 | 5.3% | 99.58% |
| Total CAPEX | $24,843,297 | 100% | 100% |

As shown in , field-applied inner coating required for this small cutback area is approximately **1,514 times** more expensive per square meter than the shop-applied coating.

### Field post-weld interior coating reliability

It is well documented that field interior joint coating quality is inferior compared to shop-applied FBE coatings. Field conditions—particularly temperature swings (±15°C), humidity variations (30–95% RH), and airborne contaminants (e.g., dust, oils, or salt aerosols)—compromise coating integrity by altering cure kinetics, adhesion properties, and overall durability. These environmental factors significantly impact the performance of field-applied coatings compared to shop-applied systems.

Thermal expansion and contraction cycles induce microcracking in partially cured coatings, while moisture ingress disrupts polymer cross-linking, creating pathways for corrosion initiation and propagation.

Airborne particulates embed into applied layers, acting as focal points for disbondment, coating failure, or accelerated degradation over time. Additionally, wind and precipitation during application further complicate proper surface preparation and curing conditions.

This environmental sensitivity explains why field-applied coatings exhibit 2.8 times more defects (e.g., delamination, pinholes, uneven thickness, incomplete coverage, or surface irregularities) than shop-applied systems. Improper surface preparation—such as inadequate blast profiles or residual mill scale and oxides—accounts for 61% of failures identified in third-party audits and inspections.

These flaws reduce coating adhesion strength by up to 40%, weaken barrier properties, and significantly accelerate localized corrosion rates in high-stress weld zones where mechanical strain is concentrated. See photo 2.

|  |  |
| --- | --- |
|  |  |
| *Photo 1.* Displays a clean adhesion test result for a factory-applied FBE coating. The uniform removal of the coating indicates strong adhesion to the substrate, achieved through controlled application processes in a factory setting with optimal surface preparation and curing conditions. | *Photo 2.* Shows the results of an adhesion test on a field-applied liquid epoxy coating near a weld seam. The presence of ferrous oxide (rust) and contamination on the reverse dolly highlights suboptimal surface preparation and environmental challenges during field application. These defects compromise coating adhesion and increase the risk of corrosion in service*.* |

Consequently, achieving reliable performance from field-applied coatings requires stringent quality control measures, including proper surface preparation, controlled application environments, detailed inspection protocols, and strict adherence to curing specifications.

As a result, achieving reliable performance from field-applied coatings requires stringent quality control measures, including proper surface preparation, controlled application environments, and adherence to curing specifications. These challenges have driven the market to innovate alternative solutions, such as:

* **FlexSleeve**®. A stiff polymer sleeve with bore seals that is inserted into pipe ends before welding.
* **SIDGMAN**®. A two-piece system—one male and one female—welded in the shop to the ends of each pipe.
* **Style X07**. A very high-pressure Victaulic coupling listed under ASME B31.4. It has been installed in two projects in Chile: 24" MLP INCO and 32" SQM TEA.

|  |
| --- |
| **A long pipe on a road  AI-generated content may be incorrect.**  Photo 3. [SQM’s TEA project](https://youtu.be/e14DHsekBIg?si=nDQ1uiHFtaoSzMGE), a 32" seawater interior FBE coated pipeline was joined by Victaulic’s X07 couplings.  The need for robot field coating was eliminated. |
|  |

# Operational Expenditures

## Corrosion inhibitors injection

While corrosion allowance provides structural buffer through increased wall thickness, active inhibition via chemical treatments proves more cost-effective for long-distance pipelines.

Experimental validation confirms a **26 ppm** sodium polyphosphate dosage achieves target corrosion rates ≤0.15 mm/year through passivation film formation. Complementary biocide protocols apply weekly 4-hour shock treatments (20 ppm glutaraldehyde equivalent to **0.46 ppm** continuous dose) for microbial control.

OPEX calculation parameters:

* + Annual operating hours: 8,400
  + Flow rate: 0.7 m³/s → 21,168,000 m³/year
  + Inhibitor cost: $1.8/kg (sodium polyphosphate)
  + Biocide cost: $12.8/kg (glutaraldehyde)

Dosage requirements derived from:

* + Continuous inhibitor: 26 ppm × 21,168,000 m³/yr   
    =  **550,368 kg/yr**
  + Biocide equivalent: 0.46 ppm × 21,168,000 m³/yr  
    =  **9,660 kg/yr**

Table . OPEX to achieve at least 0.15 mm/yr corrosion rate.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| ***Item*** | ***Dosage*** *ppm* | ***Price*** *per  kg* [10] | ***Mass*** *kg per year* | ***Cost*** *($/year)* |
| Inhibitor | 26.00 | $1.8 | 550,368 | $990,662 |
| Biocide | 0.46 | $12.8 | 9,660 | $123,648 |
| Dosing Plant3 | | | | $12,000 |
|  |  |  | Total OPEX | **$1,126,310** |

3 Service-Based Infrastructure Model: Third-party managed dosing systems replace owned infrastructure through subscription services ($1,000/month OPEX).

To compare future OPEX cash flows with CAPEX on an equal footing, future cash flows must be discounted to their present value (PV).

The present value is calculated using (3):

(3)

Where PV is the Present Value, FV is the future value (annual OPEX of $1,126,310); r is the discount rate, 10%; n is the number of years into the future. Assuming cash flows occur at the end of each period over a 25-year service life, the inhibitors' OPEX present value is calculated as $10,223,565.

Note that corrosion inhibitors for bare steel water pipelines face several significant performance limitations. The effectiveness of most inhibitors is substantially affected by water chemistry, temperature, and flow velocity, with performance deteriorating as temperatures rise and water flow increases [11].

Laboratory-tested inhibitors frequently fail to achieve the same effectiveness when deployed in real industrial applications [12].

For bare steel specifically, inhibitor coverage may be uneven, leaving vulnerable spots exposed to corrosion attack. Some inhibitors, particularly when applied at insufficient concentrations, may actually accelerate localized corrosion rather than prevent it [13].

The desorption process of inhibitors from metal surfaces is unavoidable under industrial conditions, especially at elevated temperatures and in high-flow environments [14]. Water quality variations (pH, alkalinity, dissolved ions) can significantly reduce inhibitor performance, requiring constant monitoring and adjustment. Additionally, operational processes like hydrostatic testing can elevate corrosion risks despite inhibitor presence.

## Inspections

Bare uncoated steel pipes with corrosion allowance and internally epoxy-coated pipes require distinct inspection strategies due to their differing approaches to corrosion management.

For bare steel pipes, inspections focus on monitoring wall thickness loss over time using techniques such as magnetic flux leakage (MFL) or ultrasonic testing (UT). These methods detect material degradation, with repairs involving weld patches, sleeves, or section replacements. Inspection intervals are typically every 3–5 years, with annual costs ranging from $8,000 to $15,000 per kilometer.

In contrast, internally epoxy-coated pipes require inspections to assess coating integrity using techniques like electrochemical impedance spectroscopy (EIS) or linear polarization resistance (LPR).

Repairs involve reapplying liquid epoxy to damaged areas. Coated pipes benefit from longer inspection intervals of 5–10 years and lower annual costs of $4,000 to $8,000 per kilometer.

Table summarizes the key differences in inspection methodologies, frequencies, and costs:

Table . Inspections feature comparison.

|  |  |  |
| --- | --- | --- |
| ***Concept*** | ***Bare Pipe*** | ***Coated pipe*** |
| Main Inspection Methodology | Magnetic flux leakage (MFL) and/or ultrasonic testing (UT). | Electrochemical impedance spectroscopy (EIS) and/or linear polarization resistance (LPR). |
| Repair | Weld patches, sleeves or replace entire section. | Reapply liquid epoxy to the interior surface. |
| Periodicity | 3–5 years. | 5–10 years. |
| Cost/Year | $8,000–$15,000/km | $4,000–$8,000/km |

For analytical purposes, this study assumes annual inspection costs of $8,000/km for internally FBE-coated pipes and $4,000/km for bare steel pipes. Given a pipeline length of 100 km:

* The annual OPEX for bare pipes is $800,000.
* The annual OPEX for coated pipes is $400,000.

Using a 10%, discount rate over a 25-year service life:

* The present value (PV) of inspection costs for bare pipes is $7,261,632.
* The PV of inspection costs for coated pipes is $3,630,816.

## Energy consumption

Chile's industrial electricity pricing incorporates generation costs, transmission fees, and distribution charges. The generation component reflects marginal system costs influenced by fossil fuel prices and renewable penetration.

For large industrial consumers, July 2024 data showed an average rate of $128/MWh. This baseline industrial rate of $128/MWh requires adjustment through three critical factors: fuel price volatility, renewable integration costs and transmission constraints. Chile's 2024 Tariff Stabilization Law further modifies pricing via:

* Generation component adjustments. (+15% from 2022 baseline, CPI-indexed).
* Debt servicing surcharge ($0.02/kWh until 2035).
* Transmission upgrades. ($1.2/MWh fee).

This comprehensive adjustment framework elevates the 2024 effective rate to:

It is important to note that the energy costs for the Chilean mining sector costs rose from $85/MWh (2015) to $112/MWh (2024), 40% above Peruvian competitors.

Table .Historical Price Context

|  |  |  |
| --- | --- | --- |
| **Year** | **Avg. Industrial Rate** | **Key Influencers** |
| 2022 | $145/MWh | Coal phase-out begins |
| 2023 | $158/MWh | Gas price spike |
| 2024 | $168/MWh (adjusted) | Debt repayment initiated |
| 2025 | $175/MWh (projected) | Full tariff normalization |

This analysis adopts a projected rate of P = $175/MWh for years 2025 onwards. This rate is used in (4) which calculates de cost of energy consumed by the pipeline project pump(s).

(4)

Where is fluid density; *g* is the gravitational acceleration; *Q* is the volumetric flow rate; is the total head loss due to friction losses () plus elevation head ( **= 1000 m**); is the pump efficiency (**82%**) and *t* is the annual operating time (**8400 hours**).

To estimate energy required to overcome friction losses in the pipeline the Darcy-Weisbach equation (5) is used.

(5)

Where is the head loss due to friction losses in the pipeline; f is the Darcy-Weisbach friction factor, a dimensionless parameter representing energy loss due to friction in a pipe; L is the length of the pipeline; is the velocity of the fluid; g is the acceleration due to gravity; and D is the inside diameter of the pipeline, where larger diameters reduce friction losses by lowering fluid velocity for a given flow rate.

To calculate the Darcy-Weisbach friction factor f, the Colebrook-White equation is utilized.

(6)

Where f is the Darcy-Weisbach friction factor; k is the pipe’s roughness height and D is the pipe inside diameter; Re is the Reynolds number; and the logarithmic term accounts for both surface roughness. The equation is implicit in f and requires iterative or numerical methods to solve.

***Bare Pipe Case Calculations***

For the bare pipe case, on year 1, the Reynolds number is calculated as using equation:

(7)

Where is the fluid density (**1030**), is the fluid velocity on year 1 (**1.901 m/s**) derived from the flow ratio of **0.7 m³/s**, is the pipe inside diameter (**0.68464m**) for wall thickness of **13.28** mm on year 1, is the dynamic viscosity (**0.0013 Pa·s**). Substituting values, . Again, substituting values on (6):

(8)

Solving for f using the Newton-Raphson iterative numerical technique which converges to f = 0.013396. Substituting values on eq (3):

(9)

Again, substituting values on eq (2):

(10)

= $17,247,242

For the bare pipe case, previous calculation procedure is repeated for the next 25 years, decreasing the wall thickness by the design corrosion rate of 0.15 mm/yr; from 13.28 mm on year 1 to 9.53 mm on year 25; and increasing the pipe roughness from 0.068**.** mm on first year to 0.720 mm by the end of year 25.

***Coated Pipe Case Calculations***

Same procedure is done for the coated pipe case, only this time, wall thickness is maintained at 0.015 mm, and pipe roughness increases from 0.015 mm on first year to 0.035mm by year 25 end. Results for both the bare and coated pipe are listed on Annex A – Energy Consumption Calculations.

Table . Electricity Consumption Present Value Comparison

|  |  |  |  |
| --- | --- | --- | --- |
| Energy Cost PV | Bare Pipe | Coated Pipe | Difference |
| Friction | $48,965,594 | $35,957,717 | $13,007,877 |
| Elevation | $115,054,517 | $115,054,517 | $0 |

Since the elevation cost is unrelated to corrosion and remains identical for both strategies, it will not be considered in the economic comparison. This decision ensures the analysis focuses solely on factors directly influenced by corrosion mitigation methods, such as material selection, coating application, maintenance requirements, and frictional energy losses.

# Results

## CAPEX Comparison

The corrosion allowance strategy requires 27.9% ($4.58M) more steel mass than coated systems, increasing initial CAPEX to $21.07M. While coated pipes show lower baseline steel costs ($15.20M), field joint coating adds $8.33M (33.5% of total CAPEX) due to robotic application requirements.

Notably, field-applied joint coatings cost 1,514× more per m² than shop FBE ($1,000/joint vs $6/m²), despite protecting only 0.42% of total surface area. This cost disparity stems from complex field logistics and inferior coating quality (2.8× more defects vs shop FBE).

## OPEX Comparison

Bare pipe systems incur $17.49M higher OPEX over 25 years (PV discounted at 10%):

* **Chemical Inhibitors**: $10.22M PV  
  (46% of bare pipe OPEX)
* **Energy Penalty**: $13.01M PV from increased friction  
  (0.72mm roughness vs 0.035mm coated)
* **Inspections**: $3.63M PV savings from coated systems' longer intervals

Coated systems eliminate inhibitor costs while maintaining 92% lower surface roughness, reducing pumping energy by 26.6% ($35.96M vs $48.97M PV).

## Lifecycle Cost Analysis Results

Total 25-year expenditures reveal:

* **Bare Pipe**: $72.32M (CAPEX 8.1%, OPEX 91.9%)
* **Coated Pipe**: $49.23M (CAPEX 19.6%, OPEX 80.4%)

Coated systems demonstrate $23.09M (31.9%) lifecycle savings despite 64.3% higher CAPEX. The break-even point occurs at Year 14 considering time-valued costs.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| |  |  |  |  |  | | --- | --- | --- | --- | --- | |  |  | ***Corrosion Strategy*** | |  | | ***Type*** | ***Expenditure Category*** | ***Bare*** | ***Coated*** | ***Coated Savings*** | | CAPEX | Extra Steel for Corrosion | $5,869,705 |  | $5,869,705 | | CAPEX | Field Joint Coating |  | $8,334,000 | -$8,334,000 | | CAPEX | Shop-applied Coating |  | $1,304,653 | -$1,304,653 | | OPEX | Corrosion Inhibitors | $10,223,565 |  | $10,223,565 | | OPEX | Extra Friction Energy | $48,965,594 | $35,957,717 | $13,007,877 | | OPEX | Extra Inspections | $7,261,632 | $3,630,816 | $3,630,816 | |  | **Total CAPEX** | $5,869,705 | $9,638,653 | -$3,768,948 | |  | **Total OPEX** | $66,450,791 | $39,588,533 | $26,862,258 | |  | **Total Expenditure** | $72,320,496 | $49,227,186 | $23,093,309 | |  |

# 

# Discussion

## **Interpretation of Results**

The lifecycle cost analysis of corrosion mitigation strategies for water pipelines reveals significant economic and operational implications. This interpretation delves deeper into the key findings, their underlying factors, and broader implications for pipeline design and operation.

### Energy Savings and Hydraulic Efficiency

The analysis identifies substantial energy savings of **$13.01 million (present value)** associated with internally epoxy-coated pipes compared to bare steel pipelines. This result underscores the critical role that hydraulic efficiency plays in pipeline economics:

**Surface Roughness Impact**: Internally coated pipes maintain significantly lower surface roughness (0.015–0.035 mm) throughout their service life compared to bare pipes (0.068–0.720 mm). This smoother surface directly translates into reduced frictional head losses and lower pumping energy requirements.

**Stable Internal Diameter**: Coated pipes maintain their initial internal diameter (692.14 mm) over the entire 25-year period, whereas bare pipes experience progressive diameter reduction due to corrosion-induced wall thickness increases. This difference compounds energy efficiency advantages over time.

**Regional Energy Cost Context**: Chile's elevated industrial electricity rates ($175/MWh) amplify the importance of friction-related energy savings, making hydraulic efficiency a particularly impactful economic factor in this regional context.

These factors collectively justify the higher initial capital expenditures (CAPEX) associated with coating systems, as the long-term operational expenditure (OPEX) savings from reduced pumping energy more than offset these upfront costs.

### **Field Joint Coating Challenges**

While internal epoxy coatings demonstrate clear economic advantages, the analysis highlights critical vulnerabilities associated with field joint coatings:

**Cost Disparity**: Field-applied coatings cost approximately 1,514 times more per square meter than shop-applied coatings. This stark difference stems from logistical complexities, specialized robotic equipment requirements, and challenging field conditions.

**Quality Concerns**: Field-applied coatings exhibit approximately 2.8 times more defects (e.g., delamination, pinholes, uneven thickness) compared to shop-applied coatings. These defects primarily arise from environmental factors such as temperature fluctuations (±15°C), humidity variations (30–95% RH), and airborne contaminants.

**Failure Implications**: Approximately 61% of coating failures originate at field joints, significantly reducing adhesion strength by up to 40%, weakening barrier properties, and accelerating localized corrosion—especially in high-stress weld zones.

These vulnerabilities underscore the need for stringent quality control protocols during field joint coating application. Investments in advanced robotic systems or alternative coupling technologies (such as Victaulic's X07 coupling used in Chilean projects) may effectively mitigate these risks.

### Lifecycle Cost Dynamics

The interpretation of results reveals important insights into the long-term economic performance of both strategies:

**Break-Even Point**: Despite 64.3% higher initial CAPEX, coated systems achieve break-even with bare pipe strategies by Year 14, considering time-valued costs.

**Total Savings**: Over the 25-year analysis period, coated systems demonstrate $23.09 million (31.9%) in lifecycle savings compared to bare pipe strategies.

**OPEX vs. CAPEX Balance**: For bare pipes, OPEX accounts for 91.9% of total lifecycle costs, compared to 80.4% for coated systems. This highlights the importance of considering long-term operational efficiencies in pipeline design decisions.

### Sensitivity Analysis Insights

The interpretation benefits from sensitivity analyses on key parameters:

**Energy Price Sensitivity**: Each 1% increase in electricity rates adds approximately $350,000/year to bare pipe OPEX. Given Chile's historical volatility in energy pricing, this sensitivity underscores significant financial risks associated with bare pipe strategies.

**Coating Durability Sensitivity**: A hypothetical reduction in coating service life by five years would eliminate approximately 22% of calculated lifecycle savings, emphasizing the importance of ensuring coating longevity.

**Altitude-Specific Corrosion Risks**: At elevations exceeding 3,000 meters above sea level—common in Chilean mining operations—the standard corrosion allowance (3.75 mm over 25 years) may prove insufficient against aggressive localized pitting corrosion.

These sensitivity analyses highlight critical risk factors that must be carefully managed when selecting corrosion mitigation strategies for high-altitude Chilean pipeline infrastructure.

### **Strategic Implications for Pipeline Operators**

Beyond direct cost comparisons, several strategic considerations emerge:

**Lifecycle Perspective Importance**: The superior lifecycle economics of coated systems (31.9% savings over 25 years) underscore the importance of adopting a comprehensive lifecycle perspective rather than focusing solely on upfront expenditures.

**Environmental and Regulatory Factors**: Coated systems eliminate the need for continuous chemical inhibitor treatments, potentially offering environmental and regulatory compliance advantages in sensitive ecosystems.

**Operational Flexibility**: The improved hydraulic efficiency of coated systems may provide greater operational flexibility, allowing for potential flow rate increases or reduced pumping requirements in response to changing operational needs.

This interpretation reinforces the economic and operational advantages of internally coated pipeline systems while highlighting the critical importance of addressing field joint coating challenges to fully realize these benefits in high-altitude Chilean water infrastructure projects.

## **Comparison with Existing Literature**

### Alignment with Previous Studies

The lifecycle savings of 31.9% identified in this analysis align with recent findings from industry-standard studies:

**NACE SP21430-2023** reports lifecycle cost advantages for internally coated pipelines ranging between **28% and 34%** compared to bare steel systems. The present study's result of 31.9% savings falls comfortably within this established range, reinforcing the validity of our methodology and assumptions.

Similarly, the Canadian Association of Petroleum Producers (**CAPP**, 2018) estimated lifecycle cost advantages of coated pipelines at approximately **22–25%**. While slightly lower than our calculated savings, these figures still broadly support the economic superiority of internally coated systems.

### Differences and Potential Reasons

Despite broad agreement, certain discrepancies emerge when comparing specific cost components and assumptions:

#### Energy Cost Assumptions

Our analysis assumes an electricity price of $175/MWh, significantly higher than typical North American benchmarks ($85–110/MWh) used in previous studies (e.g., CAPP 2018). This elevated energy cost scenario is specific to Chile's industrial context, driven by factors such as fossil fuel dependency, renewable integration costs, transmission constraints, and regulatory adjustments.

Consequently, our calculated energy savings ($13.01M PV) surpass those reported in studies conducted in regions with lower electricity prices. This difference highlights the sensitivity of lifecycle cost analyses to regional energy pricing dynamics.

#### Field Joint Coating Costs and Risk

Our study identifies field joint coating costs as approximately **6.4 times** higher than baseline steel costs. This ratio aligns closely with recent project audits by TYHOO Group (2023) but contrasts with earlier predictions by the IEC (2017) study, which estimated a ratio closer to **4.8 times**. The discrepancy can be attributed to recent inflationary pressures on labor costs, logistical complexities in remote high-altitude Chilean locations, and technological advancements requiring specialized robotic equipment for field coating.

Additionally, the limited market availability—with **only two specialized providers** (CRTS and Tyhoo)—represents a significant risk factor, potentially affecting service reliability, pricing stability, and availability of timely technical support during pipeline construction and maintenance activities.

#### Inspection and Maintenance Costs

The present study assumes inspection intervals and costs consistent with industry standards: bare pipes inspected every 3–5 years at $8,000–$15,000/km/year and coated pipes every 5–10 years at $4,000–$8,000/km/year.

These assumptions align well with existing literature (e.g., NACE SP21430-2023), which emphasizes reduced inspection frequency and lower maintenance expenditures as key benefits of internally coated pipelines.

### Additional Considerations from Literature

Beyond direct financial comparisons, existing literature emphasizes several qualitative factors that further support the adoption of internally coated pipeline systems:

#### Technical Reliability and Durability

Research from sources such as Al-Qahtani Pipe Coating Industries underscores the superior durability of shop-applied FBE coatings under controlled conditions compared to field-applied coatings. Our analysis confirms this finding by documenting a **2.8-fold increase** in defects for field-applied coatings compared to shop-applied coatings.

Innovations like **Victaulic's X07 coupling system**, successfully implemented in Chilean projects such as SQM's TEA pipeline and AMSA’s INCO, offer promising alternatives that eliminate the need for field joint coating altogether. This approach not only enhances pipeline reliability and reduces dependency on highly skilled welders, but also significantly lowers overall costs and accelerates pipe joining processes.

Furthermore, the coupling mitigates project risks by minimizing dependency on favorable weather conditions—unlike welding operations, which are highly sensitive to environmental factors—thus providing greater operational flexibility and predictability during pipeline construction.

#### Altitude and Operational Conditions

Literature on high-altitude pipeline corrosion indicates increased susceptibility to localized pitting corrosion at elevations above 3,000 meters due to environmental stressors like temperature fluctuations and oxygen availability.

## Summary Table: Literature Comparison Overview

|  |  |  |  |
| --- | --- | --- | --- |
| *Aspect* | *This Study Findings* | *Existing Literature Findings* | *Alignment/Discrepancy Explanation* |
| Lifecycle Cost Savings | 31.9% | NACE: 28–34%, CAPP: 22–25% | Strong alignment; minor differences due to regional factors |
| Energy Cost Assumption | $175/MWh | North America: $85–110/MWh | Discrepancy due to Chilean-specific energy market dynamics |
| Field Joint Coating Cost Ratio | 6.4× steel costs | TYHOO Group: ~6×; IEC: ~4.8× | Alignment with recent audits; discrepancy due to inflationary pressures |
| Inspection Intervals & Costs | Bare: $8k/km/yr; Coated: $4k/km/yr | Industry standard intervals & similar costs | Strong alignment |
| Environmental Impact | Eliminates chemical inhibitors | EPA highlights ecological risks | Reinforces environmental advantage of internally coated systems |
| Technical Reliability | Field joints have higher defect rate | Al-Qahtani confirms superior shop coatings | Alignment; highlights need for improved field application methods |
| Altitude Considerations | Corrosion allowance potentially insufficient at high altitudes (>3000m) | MDPE confirms increased pitting risks at high altitudes | Alignment; underscores importance of site-specific evaluations |

## Conclusion on Literature Comparison

Overall, this expanded comparison demonstrates strong consistency between our findings and existing industry literature while highlighting specific regional factors—particularly energy pricing—that influence lifecycle cost outcomes significantly.

The observed discrepancies are well-explained by contextual differences (such as geographic location and market conditions), reinforcing confidence in our results while emphasizing the importance of adapting corrosion mitigation strategies to local operational contexts.

# Summary

The lifecycle cost analysis demonstrates that internally epoxy-coated pipelines offer significant advantages over bare pipe (corrosion allowance) strategies for water transport infrastructure in Chile. Although coated systems require higher initial investments—primarily due to specialized field joint coatings—their smoother internal surfaces considerably reduce frictional energy losses, generating substantial operational savings over a 25-year period.

Bare pipe systems, despite lower upfront costs, incur higher lifecycle expenses due to increased steel usage, continuous chemical inhibitor treatments, frequent inspections, and elevated pumping energy demands. Additionally, the corrosion allowance strategy presents heightened risks at high-altitude installations (>3,000 m), where aggressive pitting corrosion can exceed standard allowances.

Overall, internally epoxy-coated pipelines emerge as economically superior, environmentally friendlier, and operationally more reliable options, provided stringent quality controls are enforced during field joint coating applications.

Appendix A

Table . Bare pipe Electricity cost calculations.

|  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Analyzed case: Bare. Initial wall thickness = 13.28 mm; year 25 wall thickness = 9.53 mm. Initial pipe roughness = 0.07 mm; year 25 pipe roughness = 0.72 mm. Fixed parameters: Elevation head = 1000 m; pump efficiency = 82%; energy cost = 175 $/MWh; outside diameter = 28''; flow rate = 700 L/s; density of water = 1030 kg/m3; viscosity of water = 0.0013 Pa·s | | | | | | | | | | |
| Yr | Pipe  roughness  [ mm ] | Interior  Diameter  [ mm ] | Wall  thickness  [ mm ] | Fluid  Velocity  [m/s] | Friction  factor f  [ ] | Head  Loss  [ m ] | Pump  Friction  [ kW ] | Pump  Elevation  [ kW ] | Electricity  Friction  [ M$ ] | Electricity  Elevation  [ M$ ] | |
| 1 | 0.100 | 682.140 | 14.53000 | 1.915 | 0.014030 | 269.32 | 2322 | 8623 | $3,413,697 | $12,675,334 | |
| 2 | 0.108 | 682.557 | 14.32167 | 1.913 | 0.014180 | 271.37 | 2340 | 8623 | $3,439,685 | $12,675,334 | |
| 3 | 0.117 | 682.973 | 14.11333 | 1.911 | 0.014325 | 273.31 | 2357 | 8623 | $3,464,266 | $12,675,334 | |
| 4 | 0.125 | 683.390 | 13.90500 | 1.908 | 0.014466 | 275.14 | 2372 | 8623 | $3,487,545 | $12,675,334 | |
| 5 | 0.133 | 683.807 | 13.69667 | 1.906 | 0.014602 | 276.89 | 2387 | 8623 | $3,509,618 | $12,675,334 | |
| 6 | 0.142 | 684.223 | 13.48833 | 1.904 | 0.014734 | 278.54 | 2402 | 8623 | $3,530,569 | $12,675,334 | |
| 7 | 0.150 | 684.640 | 13.28000 | 1.901 | 0.014862 | 280.11 | 2415 | 8623 | $3,550,473 | $12,675,334 | |
| 8 | 0.158 | 685.057 | 13.07167 | 1.899 | 0.014987 | 281.60 | 2428 | 8623 | $3,569,398 | $12,675,334 | |
| 9 | 0.167 | 685.473 | 12.86333 | 1.897 | 0.015108 | 283.02 | 2440 | 8623 | $3,587,405 | $12,675,334 | |
| 10 | 0.175 | 685.890 | 12.65500 | 1.895 | 0.015227 | 284.38 | 2452 | 8623 | $3,604,550 | $12,675,334 | |
| 11 | 0.183 | 686.307 | 12.44667 | 1.892 | 0.015342 | 285.66 | 2463 | 8623 | $3,620,882 | $12,675,334 | |
| 12 | 0.192 | 686.723 | 12.23833 | 1.890 | 0.015455 | 286.89 | 2474 | 8623 | $3,636,447 | $12,675,334 | |
| 13 | 0.200 | 687.140 | 12.03000 | 1.888 | 0.015565 | 288.06 | 2484 | 8623 | $3,651,288 | $12,675,334 | |
| 14 | 0.208 | 687.557 | 11.82167 | 1.885 | 0.015673 | 289.18 | 2493 | 8623 | $3,665,442 | $12,675,334 | |
| 15 | 0.217 | 687.973 | 11.61333 | 1.883 | 0.015778 | 290.24 | 2503 | 8623 | $3,678,945 | $12,675,334 | |
| 16 | 0.225 | 688.390 | 11.40500 | 1.881 | 0.015881 | 291.26 | 2511 | 8623 | $3,691,830 | $12,675,334 | |
| 17 | 0.233 | 688.807 | 11.19667 | 1.879 | 0.015983 | 292.23 | 2520 | 8623 | $3,704,127 | $12,675,334 | |
| 18 | 0.242 | 689.223 | 10.98833 | 1.876 | 0.016082 | 293.16 | 2528 | 8623 | $3,715,863 | $12,675,334 | |
| 19 | 0.250 | 689.640 | 10.78000 | 1.874 | 0.016179 | 294.04 | 2535 | 8623 | $3,727,065 | $12,675,334 | |
| 20 | 0.258 | 690.057 | 10.57167 | 1.872 | 0.016275 | 294.88 | 2543 | 8623 | $3,737,757 | $12,675,334 | |
| 21 | 0.267 | 690.473 | 10.36333 | 1.869 | 0.016368 | 295.69 | 2550 | 8623 | $3,747,962 | $12,675,334 | |
| 22 | 0.275 | 690.890 | 10.15500 | 1.867 | 0.016461 | 296.46 | 2556 | 8623 | $3,757,699 | $12,675,334 | |
| 23 | 0.283 | 691.307 | 9.94667 | 1.865 | 0.016551 | 297.19 | 2563 | 8623 | $3,766,990 | $12,675,334 | |
| 24 | 0.292 | 691.723 | 9.73833 | 1.863 | 0.016640 | 297.89 | 2569 | 8623 | $3,775,852 | $12,675,334 | |
| 25 | 0.300 | 692.140 | 9.53000 | 1.860 | 0.016728 | 298.56 | 2574 | 8623 | $3,784,304 | $12,675,334 | |
|  | Bare Pipe Case. Present Value (annual OPEX discounted at 10% rate) | | | | | | | | $32,323,586 | $115,054,517 | |

Table . Coated pipe Electricity cost calculations

|  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Analyzed case: Coated. Initial wall thickness = 9.53 mm; year 25 wall thickness = 9.53 mm. Initial pipe roughness = 0.02 mm; year 25 pipe roughness = 0.04 mm. Fixed parameters: Elevation head = 1000 m; pump efficiency = 82%; energy cost = 175 $/kWh; outside diameter = 28''; flow rate = 700 L/s; density of water = 1030 kg/m3; viscosity of water = 0.0013 Pa·s | | | | | | | | | | |
| Yr | **Pipe**  **roughness**  **[ mm ]** | **Interior**  **Diameter**  **[ mm ]** | **Wall**  **thickness**  **[ mm ]** | **Fluid**  **Velocity**  **[m/s]** | **Friction**  **factor**  **f** | **Head**  **Loss**  **[ m ]** | **Pump**  **Friction**  **[ kW ]** | **Pump**  **Elevation**  **[ kW ]** | **Electricity**  **Friction**  **[ M$ ]** | **Electricity**  **Elevation**  **[ M$ ]** |
| 1 | 0.0100 | 692.140 | 9.53000 | 1.860 | 0.011929 | 212.91 | 1836 | 8623 | $2,698,730 | $12,675,334 |
| 2 | 0.0117 | 692.140 | 9.53000 | 1.860 | 0.011980 | 213.83 | 1844 | 8623 | $2,710,311 | $12,675,334 |
| 3 | 0.0133 | 692.140 | 9.53000 | 1.860 | 0.012031 | 214.73 | 1852 | 8623 | $2,721,728 | $12,675,334 |
| 4 | 0.0150 | 692.140 | 9.53000 | 1.860 | 0.012080 | 215.61 | 1859 | 8623 | $2,732,985 | $12,675,334 |
| 5 | 0.0167 | 692.140 | 9.53000 | 1.860 | 0.012130 | 216.49 | 1867 | 8623 | $2,744,089 | $12,675,334 |
| 6 | 0.0183 | 692.140 | 9.53000 | 1.860 | 0.012178 | 217.35 | 1874 | 8623 | $2,755,043 | $12,675,334 |
| 7 | 0.0200 | 692.140 | 9.53000 | 1.860 | 0.012226 | 218.21 | 1882 | 8623 | $2,765,852 | $12,675,334 |
| 8 | 0.0217 | 692.140 | 9.53000 | 1.860 | 0.012273 | 219.05 | 1889 | 8623 | $2,776,522 | $12,675,334 |
| 9 | 0.0233 | 692.140 | 9.53000 | 1.860 | 0.012319 | 219.88 | 1896 | 8623 | $2,787,055 | $12,675,334 |
| 10 | 0.0250 | 692.140 | 9.53000 | 1.860 | 0.012365 | 220.70 | 1903 | 8623 | $2,797,457 | $12,675,334 |
| 11 | 0.0267 | 692.140 | 9.53000 | 1.860 | 0.012411 | 221.51 | 1910 | 8623 | $2,807,731 | $12,675,334 |
| 12 | 0.0283 | 692.140 | 9.53000 | 1.860 | 0.012456 | 222.31 | 1917 | 8623 | $2,817,880 | $12,675,334 |
| 13 | 0.0300 | 692.140 | 9.53000 | 1.860 | 0.012500 | 223.10 | 1924 | 8623 | $2,827,908 | $12,675,334 |
| 14 | 0.0317 | 692.140 | 9.53000 | 1.860 | 0.012544 | 223.89 | 1930 | 8623 | $2,837,819 | $12,675,334 |
| 15 | 0.0333 | 692.140 | 9.53000 | 1.860 | 0.012587 | 224.66 | 1937 | 8623 | $2,847,616 | $12,675,334 |
| 16 | 0.0350 | 692.140 | 9.53000 | 1.860 | 0.012630 | 225.42 | 1944 | 8623 | $2,857,302 | $12,675,334 |
| 17 | 0.0367 | 692.140 | 9.53000 | 1.860 | 0.012672 | 226.18 | 1950 | 8623 | $2,866,879 | $12,675,334 |
| 18 | 0.0383 | 692.140 | 9.53000 | 1.860 | 0.012714 | 226.93 | 1957 | 8623 | $2,876,351 | $12,675,334 |
| 19 | 0.0400 | 692.140 | 9.53000 | 1.860 | 0.012756 | 227.66 | 1963 | 8623 | $2,885,721 | $12,675,334 |
| 20 | 0.0417 | 692.140 | 9.53000 | 1.860 | 0.012797 | 228.40 | 1969 | 8623 | $2,894,990 | $12,675,334 |
| 21 | 0.0433 | 692.140 | 9.53000 | 1.860 | 0.012837 | 229.12 | 1976 | 8623 | $2,904,163 | $12,675,334 |
| 22 | 0.0450 | 692.140 | 9.53000 | 1.860 | 0.012877 | 229.84 | 1982 | 8623 | $2,913,240 | $12,675,334 |
| 23 | 0.0467 | 692.140 | 9.53000 | 1.860 | 0.012917 | 230.54 | 1988 | 8623 | $2,922,224 | $12,675,334 |
| 24 | 0.0483 | 692.140 | 9.53000 | 1.860 | 0.012956 | 231.25 | 1994 | 8623 | $2,931,118 | $12,675,334 |
| 25 | 0.0500 | 692.140 | 9.53000 | 1.860 | 0.012995 | 231.94 | 2000 | 8623 | $2,939,924 | $12,675,334 |
| Bare Pipe Case. Present Value (annual OPEX discounted at 10% rate) | | | | | | | | | **$25,223,188** | **$115,054,517** |

Table . Cost components for robotic field coating

|  |  |
| --- | --- |
| ***Cost Component*** | ***Cost per Joint*** |
| Mobilization of Crew & Equipment | $22.08 |
| Demobilization of Crew & Equipment | $13.80 |
| Personnel & Robotic Equipment | $505.08 |
| Pre-blasting Personnel & Equipment | $149.04 |
| Internal Coating Application | $181.24 |
| Pipe-End Pre-blasting | $48.76 |
| Total Cost per Joint | $1,000.00 |

References

|  |  |
| --- | --- |
| [1] | Trident Steel, "Price of Carbon Steel Seamless Pipe including ASTM A106 Grade B, ASTM A53 Gr.B, API 5L," March 2024. [Online]. Available: https://www.tridentsteel.co.in/carbon-steel-pipe-price-list.html. |
| [2] | Daiwa Lance, "Rising HRC Prices in Northern Europe," February 2025. [Online]. Available: https://www.daiwalance.com.vn/blog/rising-hrc-prices-in-northern-europe-13th-february-2025. |
| [3] | GMK Center, "Hot-rolled coil prices have increased in most markets since the beginning of the year," February 2025. [Online]. Available: https://gmk.center/en/posts/hot-rolled-coil-prices-have-increased-in-most-markets-since-the-beginning-of-the-year/. |
| [4] | SunSirs, "China Hot rolled coil Spot Price," Feb 2025. [Online]. Available: https://www.sunsirs.com/uk/prodetail-195.html. |
| [5] | US EPA, "Corrosion Manual for Internal Corrosion of Water Distribution Systems," April 1984. [Online]. Available: https://nepis.epa.gov/Exe/ZyNET.exe/10003FIW.TXT?ZyActionD=ZyDocument&Client=EPA&Index=1981+Thru+1985&Docs=&Query=&Time=&EndTime=&SearchMethod=1&TocRestrict=n&Toc=&TocEntry=&QField=&QFieldYear=&QFieldMonth=&QFieldDay=&IntQFieldOp=0&ExtQFieldOp=0&XmlQuery=. |
| [6] | MDPE, "Corrosion and Protection of Steels in Marine Environments," 2022. [Online]. Available: https://mdpi-res.com/bookfiles/book/6434/Corrosion\_and\_Protection\_of\_Steels\_in\_Marine\_Environments\_StateoftheArt\_and\_Emerging\_Research\_Trends.pdf?v=1737165901. |
| [7] | 3M, "FBE, a Foundation for Pipeline Corrosion Coatings," 2001. [Online]. Available: https://www.researchgate.net/profile/David-Enos/publication/254544412\_FBE\_a\_Foundation\_for\_Pipeline\_Corrosion\_Coatings/links/568bb8a208ae1e63f1fdd67e/FBE-a-Foundation-for-Pipeline-Corrosion-Coatings.pdf?\_\_cf\_chl\_tk=vV8pbqtPGngINgwsxZcPGcgWPLAxALNNOH.y7cWb. |
| [8] | Confidential, Interviewee, *FBE 625 MICRES coating.* [Interview]. March 2025. |
| [9] | Confidential, *Internal Girth Weld Coating · Firm Proposal,* 2024. |
| [10] | Confidential, *Tratamiento Aguas Acueducto,* 2022. |
| [11] | TYHOO Group, "Internal Field Joint Coating Robot," 2023. [Online]. Available: https://www.tyhoogroup.com/index.php/default/category/25.html. |
| [12] | CRTS,, "Robotic Internally Coated Field Joints," April 2007. [Online]. Available: https://www.iecengenharia.com.br/wp-content/uploads/2017/11/bt\_img/crts---completo.pdf. |
| [13] | Al-Qahtani, "Internal Fusion Bonded Epoxy Coating," [Online]. Available: https://ahqsons.com/al-qahtani-pipe-coating-industries/. |
| [14] | CAPP, "Mitigation of External Corrosion on Buried Carbon Steel Pipeline Systems," July 2018. [Online]. Available: https://www.capp.ca/wp-content/uploads/2024/01/Mitigation\_of\_External\_Corrosion\_on\_Buried\_Carbon\_Steel\_Pipeline\_Syst-322047.pdf. |
| [15] | IEC, "Internal Field Joint Coating," 2022. [Online]. Available: https://www.iecengenharia.com.br/wp-content/uploads/2017/11/bt\_img/crts---completo.pdf. |
| [16] | NACE, "International studies on pipeline corrosion failure rates," [Online]. Available: http://impact.nace.org/documents/ccsupp.pdf. |
| [17] | LPS, "FlexSleeve Innovation," 2023. [Online]. Available: https://www.linedpipesystems.com/lps-bd-flexsleeve-comparison/. |
| [18] | ASICORP, "Sidgman welded coupling," 2022. [Online]. Available: https://www.asicorp.cl/en/sidgman-welded-flange/. |
| [19] | JPCL, "Using Robotic Crawlers to Coat Interior Pipeline Girth Welds," 2011. [Online]. Available: https://www.paintsquare.com/article/download/2011-02\_PipelineCrawlers.pdf. |
| [20] | E. Vaca-Cortés, "ADHESION TESTING OF EPOXY COATING," 1998. [Online]. Available: https://fsel.engr.utexas.edu/pdfs/1265\_6.pdf. |
| [21] | M. Chauviere, "CUI Myth: Shop Coatings are Better Quality than Field Coatings," 2019. [Online]. Available: https://www.corrosionpedia.com/2/1969/corrosion/type-of-corrosion/cui-myth-2-shop-coatings-are-better-quality. |
| [22] | MP, "Coatings & Linings Field Joint Coatings," 2020. [Online]. Available: https://www.materialsperformance.com/articles/coating-linings/2018/08/field-joint-coatings. |
| [23] | Future Energy Steel, "Anti-Corrosion Protection for Pipeline Field Joint Coatings," [Online]. Available: https://energy-steel.com/anti-corrosion-protection-for-pipeline-field-joint-coatings/. |
| [24] | R. B. Eckert, "Case Histories Internal Corrosion Failures: Are We Learning from the Past?," 2017. [Online]. Available: https://www.materialsperformance.com/articles/chemical-treatment/2017/01/internal-corrosion-failures-are-we-learning-from-the-past. |
| [25] | "Internal corrosion: one of the leading causes of pipeline failure," 2006. [Online]. Available: https://cdn.prod.website-files.com/615499fb78247e406279d3ab/615499fb78247e87cf79d84c\_Ultracorr\_Internal\_Corrosion.pdf. |
| [26] | D. A. Yeshanew, "Internal Corrosion Damage Mechanisms of the Underground Water Pipelines," 2022. [Online]. Available: https://www.astrj.com/pdf-149369-75647?filename=Internal+Corrosion+Damage.pdf. |
| [27] | Mysteel Global, "WEEKLY: China's HRC export prices hold steady amid cautious mood," Feb 2025. [Online]. Available: https://www.mysteel.net/market-insights/5077817-weekly-chinas-hrc-export-prices-hold-steady-amid-cautious-mood. |
| [28] | SteelBenchmarker, "Price History," 10 Feb 2025. [Online]. Available: http://steelbenchmarker.com/history.pdf. |
| [29] | M. Abdelkader, "Automation in a robotic pipe coating system," 2021. [Online]. Available: https://patents.google.com/patent/WO2022005825A1/en. |
| [30] | C. Smith, "Land pipeline construction costs hit record $10.7 million/mile," June 2023. [Online]. Available: https://www.ogj.com/pipelines-transportation/pipelines/article/14299952/land-pipeline-construction-costs-hit-record-107-million-mile. |
| [31] | C. Stella, "Water supply for mining industry: The Chile case," March 2023. [Online]. Available: https://www.adlittle.com/en/insights/viewpoints/water-supply-mining-industry-chile-case. |

1. This is a living document, designed to improve through collaboration. Whether you have detailed technical knowledge, practical experience, or constructive feedback, your input is welcome. We encourage readers to share their insights and suggestions by [opening an issue](https://github.com/ignaciomella/Bare-vs-Coated-Water-Pipelines/issues) through the [GitHub repository](https://github.com/ignaciomella/Bare-vs-Coated-Water-Pipelines). [↑](#footnote-ref-1)
2. I.Mella works for Victaulic as Engineering Specialist based in Santiago, Chile. ([+56992400283](https://wa.me/56992400283) · imella@victaulic.com · jimella@uc.cl)

   © 2025 I.Mella. This is an open access article distributed under the terms of the creative commons attribution license (cc-by 4.0), which permits the user to copy, distribute, and transmit the work provided that the original author(s) and source are credited. [↑](#footnote-ref-2)