## Parameters
Variable name | Parameter | Value | Unit | SI base unit | Arbitrary | Reference 1 | Reference 2 | Average | Comments
pipeline_length | Pipeline Length | 100000 | m | TRUE | TRUE
pipeline_length_km | Pipeline Length | 100 | km | FALSE | FALSE
elevation_change | Elevation change | 1000 | m | TRUE | TRUE
segment_length | Segment length | 12 | m | TRUE | TRUE
outside_diameter_inches | Outside diameter | 28 | inches | FALSE | TRUE
outside_diameter | Outside diameter | 0.7112 | m | TRUE | FALSE
wall_corrosion_rate_mm_yr | Wall corrosion rate | 0.15 | mm/yr | FALSE | TRUE | https://nepis.epa.gov/Exe/ZyPURL.cgi?Dockey=10003FIW.TXT |  |  | The 0.15 mm/year corrosion rate assumption holds validity for industrial water systems with adequate treatment (pH 7–8.5, inhibitor dosing). However, seawater models require adjustment to 0.25–0.35 mm/year baseline rates with additional 0.12–0.18 mm/year biofouling roughness increments.
fbe_wall__yr_1_mm | FBE wall year 1 | 9.53 | mm | FALSE | TRUE
bare_wall__yr_1_mm | Bare wall year 1 | 13.28 | mm | FALSE | FALSE
extra wall (bare - fbe) |  | 3.75 | mm
bare_inside_diameter_yr_1 | Bare Inside Diameter year 1 | 0.68464 | m | TRUE | FALSE
fbe_inside_diameter_yr_1 | FBE Inside Diameter year 1 | 0.69214 | m | TRUE | FALSE
design_flow_rate_l_s | Design flow rate | 700 | L/s | FALSE | TRUE
design_flow_rate_m3_s | Design flow rate | 0.7 | m³/s | FALSE | FALSE
x70_steel_density | X70 Steel density | 7850 | kg/m³ | TRUE | TRUE
fluid_density | Fluid density | 1030 | kg/m³ | TRUE | TRUE
dynamic_viscosity_of_water | Dynamic viscosity of water | 0.0013 | Pa·s | TRUE | TRUE
roughness_bare_yr_1_mm | Roughness bare year 1 | 0.025 | mm | FALSE | FALSE | https://www.pipeflow.com/pipe-pressure-drop-calculations/pipe-roughness |  | 0.068 | New commercial steel (0.045–0.09 mm)
roughness_bare_yr_25_mm | Roughness bare year 25 | 0.3 | mm | FALSE | FALSE | https://apps.dtic.mil/sti/tr/pdf/ADA194321.pdf | JRI: Los cálculos de las curvas características del sistema se realizan para los escenarios de tubería nueva y usada, considerando respectivamente rugosidad (ε) igual a 0.025 mm y 0.3 mm. | 0.72 | Field data from carbon steel water mains show roughness growth rates of 0.0055–0.0518 mm/yr, yielding 0.14–1.3 mm over 25 years.
roughness_fbe_yr_1_mm | Roughness FBE year 1 | 0.015 | mm | FALSE | FALSE | https://www.steelmains.com/files/TWT%2015140%20Comparison%20of%20Sintakote%20vs%20Epoxy%20coatings%20on%20steel%20water%20pipe.pdf |  |  | The 0.015 mm value reflects field conditions with minor surface imperfections, aligning with coated pipe database
roughness_fbe_yr_25_mm | Roughness FBE year 25 | 0.035 | mm | FALSE | FALSE | https://www.imia.com/wp-content/uploads/2023/08/IMIA-WGP-126-22-Coating-Failures.pdf |  |  | Terminal roughness of 0.035 mm better reflects seawater ageing dynamics while remaining within ISO 21809-2 tolerances
interior_fbe_thickness_µm | Interior FBE thickness | 500 | µm | FALSE | FALSE | NEEDED
service_life_yr | Service life | 25 | yr | FALSE | TRUE
annual_hours_of_operation_h_yr | Annual hours of operation | 8400 | h/yr | FALSE | TRUE
pump_efficiency_percent | Pump efficiency | 82 | % | FALSE | TRUE
pump_efficiency | Pump efficiency | 0.82 |  | TRUE | FALSE
annual_discount_rate_percent | Annual discount Rate | 10 | % | FALSE | TRUE
annual_discount_rate | Annual discount Rate | 0.1 | % | TRUE | FALSE
hrc_price_usd_t | HRC price | 470 | $/t | FALSE | FALSE
field_internal_joint_coating_service_usd_joint | Field internal joint coating service | 1000 | $/joint | FALSE | FALSE | Confidential Quote
electrical_energy_usd_mwh | Electrical energy | 175 | $/MWh | FALSE | FALSE
gravitational_acceleration | Gravitational acceleration | 9.8066 | m/s² | TRUE | FALSE
| HRC to X70 value added multiplier | 1.6
| Cost per interior Surface Area (CPS) | 9 | $/m²

## Steel
Parameter | Value | Unit | SI base unit | Arbitrary
X70 Steel density | 7850 | kg/m³ | TRUE
Bare wall yr 1 | 13.28 | mm | FALSE
Outside diameter | 0.7112 | m | TRUE
Length of pipeline | 100000 | m | TRUE
hot-rolled steel coil (hrc) price | 0.47 | $/kg | FALSE
China Inland | 15 | $/t | FALSE
Ocean Freight | 120 | $/t | FALSE
Chile Inland | 35 | $/t | FALSE
Freight cost | 170 | $/t
Freight cost | 0.17 | $/kg | FALSE
Cost per weight (CPW) | 0.922 | $/kg | FALSE
Cost per weight (CPW) | 922 | $/t
Bare · Inside Diameter Yr 1 | 0.68464 | m | TRUE
Bare · Volume of 1 m of pipe | 0.029117 | m³ | TRUE |  |  | FOB
Bare · Steel weight of pipes | 22857.2116 | t |  |  | 20" API 5L | 0.8 | $/kg
Bare · Steel weight of pipes | 22857211.5784 | kg | TRUE |  | FBE interior | 0.1 | $/kg
Cost of bare pipes | 21074349.0753 | $ |  |  | 3LPE ext | 0.1 | $/kg
[5 empty] | Freight | 0.17 | $/kg
1.17
Parameter | Value | Unit | SI base unit | Arbitrary
X70 Steel density | 7850 | kg/m³ | TRUE
FBE wall yr 1 | 9.53 | mm | FALSE
FBE · Inside Diameter Yr 1 | 0.69214 | m | TRUE
FBE · Volume of 1 m of pipe | 0.021008 | m³ | TRUE
FBE · Steel weight of pipes | 16490.9372 | t
FBE · Steel weight of pipes | 16490937.2324 | kg | TRUE
Cost of FBE pipes | 15204644.1282 | $
| Bare | Coated | Extra wall thickness | Diff/Bare
Initial wall thickness | 13.28 | 9.53 |  | 69.86%
Steel Weight | 22857.2116 | 16490.9372 | 27.85%
Base steel | 15204644.1282 | 15204644.1282 | -10621232.2853
Corrosion Extra Steel | 4583411.8429 | 0
Strategy | Steel cost | Percentage
Bare | 21074349.0753 | 100%
FBE | 15204644.1282 | 72.15%
Difference | 5869704.947 | 27.85%
CFR BODEGAS LAMPA | [7 empty] | 0.35296 | 0 | -2441015.556
Date | Wall [ mm ] | Item | Descr | Qty. [ m ] | External Coating | Inner Coating | NPS | Price | Volume | Weight | CPW | FBE extra
2025-02-27 | 15.88 | 1 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH 30 (THK=15.88mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: BARED | 19644 | 3LPE THK=3.0MM | BARED | 28 | 2441015.556 | 344.6007 | 2705115.8787 | 0.90237
2025-02-27 | 12.7 | 2 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH XS (THK=12.70mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: BARED | 25836 | 3LPE THK=3.0MM | BARED | 28 | 2579293.7695 | 363.2834 | 2851774.8504 | 0.90445
2025-02-27 | 9.53 | 3 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH STD (THK=9.53mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: BARED | 24540 | 3LPE THK=3.0MM | BARED | 28 | 1846740.056 | 259.5133 | 2037179.0477 | 0.90652
2025-02-27 |  | 4 | [5 empty] | 6867049.3815
2025-02-27 | 15.88 | 5 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH 30 (THK=15.88mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: FUSION-BONDED EPOXY (FBE) ACC. TO AWWA C213 DFT=625 MICRONS | 19644 | 3LPE THK=3.0MM | FBE 625MICRES | 28 | 2725760.142 | 344.6007 | 2705115.8787 | 1.0076
2025-02-27 | 12.7 | 6 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH XS (THK=12.70mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: FUSION-BONDED EPOXY (FBE) ACC. TO AWWA C213 DFT=625 MICRONS | 25836 | 3LPE THK=3.0MM | FBE 625MICRES | 28 | 2880168.5185 | 363.2834 | 2851774.8504 | 1.01
2025-02-27 | 9.53 | 7 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH STD (THK=9.53mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: FUSION-BONDED EPOXY (FBE) ACC. TO AWWA C213 DFT=625 MICRONS | 24540 | 3LPE THK=3.0MM | FBE 625MICRES | 28 | 2062162.3785 | 259.5133 | 2037179.0477 | 1.0123
2025-02-27 |  | 8 | [5 empty] | 7668091.039 |  |  |  | -11.67%
2025-02-27 | 15.88 | 9 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH 30 (THK=15.88mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: 100% SOLIDS POLYURETHANE ACC. TO AWWA C222 DFT=625 MICRONS | 19644 | 3LPE THK=3.0MM | 100%SOL.PU 625MICRES | 28 | 3066666.974 | 344.6007 | 2705115.8787 | 1.1337
2025-02-27 | 12.7 | 10 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH 30 (THK=12.70mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: 100% SOLIDS POLYURETHANE ACC. TO AWWA C222 DFT=625 MICRONS | 25836 | 3LPE THK=3.0MM | 100%SOL.PU 625MICRES | 28 | 3240386.9785 | 363.2834 | 2851774.8504 | 1.1363
2025-02-27 | 9.53 | 11 | PIPE API 5L GRADE X65M PSL2 SAWL ASME B36.10 SCH 30 (THK=9.53mm) BE NPS 28" EXTERNAL COATING: 3LPE EXTRUDED TYPE N ACC. TO DIN 30670:2012 THK=3.0mm INNER COATING: 100% SOLIDS POLYURETHANE ACC. TO AWWA C222 DFT=625 MICRONS | 24540 | 3LPE THK=3.0MM | 100%SOL.PU 625MICRES | 28 | 2320074.008 | 259.5133 | 2037179.0477 | 1.1389
2025-02-27 |  | 12 | [5 empty] | 8627127.9605

## SC
Parameter | Value | Unit
Cost per interior Surface Area (CPS) | 6 | $/m²
Inside Diameter (D) | 0.69214 | m
Pipeline Liength (L) | 100000 | m
FBE pipeline Inner Surface (pi·D·L) | 217442.1939 | m²
Shop coating | 1304653.1636
Steel cost | 15204644.1282
16509297.2918
FBE percentage | 7.903%
Steel Percentage | 92.1%
Note on I7: Ignacio Mella: The capital cost determination relies on unit costs of US$ 2/kg for steel pipe and US$ 125/m for FBE coating.

## FJC
Cost Component | Cost per Joint
Mobilization of Crew & Equipment | 24 | 0.024
Demobilization of Crew & Equipment | 15 | 0.015 | 8.6
Personnel & Robotic Equipment | 549 | 0.549
Pre-blasting Personnel & Equipment | 162 | 0.162
Internal Coating Application | 197 | 0.197
Pipe-End Pre-blasting | 53 | 0.053
Total Cost per Joint | 1000 | 1
Pipeline Length | 100000
Segment length | 12
Joints | 8334
Total Field Internal Coating | 8334000
Cutback 0.5 m uncoated | 0.42%
Rest of the pipe coated | 99.58%
Times more expensive | 6.4
Times more expensive per surface area | 1513.5418
Total steel cost | 15204644.1282 | 61.2%
Field joint coating | 8334000 | 33.55%
Shop FBE coating | 1304653.1636 | 5.252%
Total Field Shop Steel | 24843297.2918

## Inhibitors
Parameter | Value | Unit
Flow rate | 0.7 | m³/s
Flow rate | 2520 | m³/hr
Flow rate | 1814400 | m³/month
Annual hours of operation | 8400 | hr/yr
Total volume | 21168000 | m³
Fluid density | 1030 | kg/m³
Discount Rate | 10%
Descuento por volumen | 20%
Compound | Dosage | Mass [ kg/yr ] | Price [ $/kg ] | Total | Mass [ kg/month ]
Inhibitor | 26 | 550368 | 1.8 | 990662.4 | 45864
Biocide | 0.45635 | 9660 | 12.8 | 123648 | 805
Dosing plant |  |  |  | 12000
Total |  |  |  | 1126310.4
|  |  | Present Value | 10223564.5737

## Inspections
Parameter | Value | Unit
Bare inspection cost | 8000 | $/km
FBE inspection cost | 4000 | $/km
Bare annual Inspection | 800000
FBE annual Inspection | 400000
Bare PV Inspection | 7261632.0146
FBE PV Inspection | 3630816.0073

## Electricity
|  |  | Pipeline Length | 100000 | m
|  |  | Flow rate | 0.7 | m³/s
|  |  | Fluid Density | 1030
|  |  | Elevation | 1000 | m
|  |  | Pump efficiency | 0.82
|  |  | Annual hours of operation | 8400 | hr/yr
|  |  | Projected Price of electricity | 175 | $/MWh
|  |  | Projected Price of electricity | 0.175 | $/kWh
|  |  | Projected Price of electricity | 0.000175 | $/Wh
|  |  | Bare pipe Cost of Electricity Year 1 | 16892256.3861
Analyzed case: Bare. Initial wall thickness = 13.28 mm; year 25 wall thickness = 9.53 mm. Initial pipe roughness = 0.03 mm; year 25 pipe roughness = 0.3 mm. Fixed parameters: Elevation head = 1000 m; pump efficiency = 82%; energy cost = 175 $/MWh; outside diameter = 28''; flow rate = 700 L/s; density of water = 1030 kg/m3; viscosity of water = 0.0013 Pa·s
Analyzed case: Coated. Initial wall thickness = 9.53 mm; year 25 wall thickness = 9.53 mm. Initial pipe roughness = 0.02 mm; year 25 pipe roughness = 0.04 mm. Fixed parameters: Elevation head = 1000 m; pump efficiency = 82%; energy cost = 175 $/kWh; outside diameter = 28''; flow rate = 700 L/s; density of water = 1030 kg/m3; viscosity of water = 0.0013 Pa·s
Yr | Pipe roughness [ mm ] | Interior Diameter [ mm ] | Wall thickness [ mm ] | Fluid Velocity [m/s] | Friction factor f [ ] | Head Loss [ m ] | Pump Friction [ kW ] | Pump Elevation [ kW ] | Electricity Friction [ M$ ] | Electricity Elevation [ M$ ] | Viscosity [ Pa·s ] | Outside Diameter [m] | Wall thickness [m] | Inside Diameter [m] | Pipe roughness [m] | Reynolds Number Re | Flow [L/s] | Density kg/m3 | Flow Rate [m3/s] | Eq Left Side | Eq Right Side | f diff Error | C | Year | 1
1 | 0.025 | 684.64 | 13.28 | 1.9014 | 0.012356 | 332.6872 | 2868.6545 | 8622.6764 | 4216922.0745 | 12675334.3116 | 0.0013 | 0.7112 | 0.01328 | 0.68464 | 2.5e-05 | 1031430.0067 | 700 | 1030 | 0.7 | 8.9962 | 8.9962 | 0
2 | 0.036458 | 684.9525 | 13.1237 | 1.8997 | 0.012662 | 340.1467 | 2932.975 | 8622.6764 | 4311473.3231 | 12675334.3116 | 0.0013 | 0.7112 | 0.013124 | 0.68495 | 3.6458e-05 | 1030959.4312 | 700 | 1030 | 0.7 | 8.8869 | 8.8869 | 0 |  | Density | 1030 | kg/m3 | Bare pipe
3 | 0.047917 | 685.265 | 12.9675 | 1.898 | 0.012945 | 346.9523 | 2991.6575 | 8622.6764 | 4397736.4784 | 12675334.3116 | 0.0013 | 0.7112 | 0.012967 | 0.68527 | 4.7917e-05 | 1030489.2849 | 700 | 1030 | 0.7 | 8.7892 | 8.7892 | 0 | 0.7 | Flow | 0.7 | m3/s | FBE coated
4 | 0.059375 | 685.5775 | 12.8112 | 1.8962 | 0.013208 | 353.2089 | 3045.6056 | 8622.6764 | 4477040.2672 | 12675334.3116 | 0.0013 | 0.7112 | 0.012811 | 0.68558 | 5.9375e-05 | 1030019.5672 | 700 | 1030 | 0.7 | 8.7011 | 8.7011 | 0 |  | Viscosity | 0.0013 | Pa·s
5 | 0.070833 | 685.89 | 12.655 | 1.8945 | 0.013455 | 358.997 | 3095.5152 | 8622.6764 | 4550407.3725 | 12675334.3116 | 0.0013 | 0.7112 | 0.012655 | 0.68589 | 7.0833e-05 | 1029550.2775 | 700 | 1030 | 0.7 | 8.6209 | 8.6209 | 0 |  | Exterior Diameter | 0.7112 | m
6 | 0.082292 | 686.2025 | 12.4987 | 1.8928 | 0.013688 | 364.3803 | 3141.9336 | 8622.6764 | 4618642.4467 | 12675334.3116 | 0.0013 | 0.7112 | 0.012499 | 0.6862 | 8.2292e-05 | 1029081.4152 | 700 | 1030 | 0.7 | 8.5472 | 8.5472 | 0 |  | Interior Diameter | 0.68464 | m
7 | 0.09375 | 686.515 | 12.3425 | 1.8911 | 0.013909 | 369.4096 | 3185.2997 | 8622.6764 | 4682390.5817 | 12675334.3116 | 0.0013 | 0.7112 | 0.012342 | 0.68652 | 9.375e-05 | 1028612.9798 | 700 | 1030 | 0.7 | 8.4792 | 8.4792 | 0 |  | Wall thickness | 0.01328 | m
8 | 0.10521 | 686.8275 | 12.1862 | 1.8894 | 0.014119 | 374.1264 | 3225.971 | 8622.6764 | 4742177.3664 | 12675334.3116 | 0.0013 | 0.7112 | 0.012186 | 0.68683 | 0.00010521 | 1028144.9706 | 700 | 1030 | 0.7 | 8.416 | 8.416 | 0 |  | Rougness | 2.5e-05 | m
9 | 0.11667 | 687.14 | 12.03 | 1.8876 | 0.014319 | 378.5649 | 3264.2429 | 8622.6764 | 4798437.0751 | 12675334.3116 | 0.0013 | 0.7112 | 0.01203 | 0.68714 | 0.00011667 | 1027677.3872 | 700 | 1030 | 0.7 | 8.357 | 8.357 | 0 |  | Velocity | 1.9014 | m/s
10 | 0.12812 | 687.4525 | 11.8737 | 1.8859 | 0.01451 | 382.7538 | 3300.3626 | 8622.6764 | 4851532.9722 | 12675334.3116 | 0.0013 | 0.7112 | 0.011874 | 0.68745 | 0.00012812 | 1027210.2288 | 700 | 1030 | 0.7 | 8.3017 | 8.3017 | 0 |  | Reynolds Number | 1031430.0067 | m
11 | 0.13958 | 687.765 | 11.7175 | 1.8842 | 0.014694 | 386.7174 | 3334.5389 | 8622.6764 | 4901772.2403 | 12675334.3116 | 0.0013 | 0.7112 | 0.011717 | 0.68777 | 0.00013958 | 1026743.495 | 700 | 1030 | 0.7 | 8.2497 | 8.2497 | 0 |  | Friction factor | 0.012356
12 | 0.15104 | 688.0775 | 11.5612 | 1.8825 | 0.01487 | 390.4763 | 3366.9504 | 8622.6764 | 4949417.1585 | 12675334.3116 | 0.0013 | 0.7112 | 0.011561 | 0.68808 | 0.00015104 | 1026277.1851 | 700 | 1030 | 0.7 | 8.2005 | 8.2005 | 0 |  | Friction Head Loss | 332.6872 | m
13 | 0.1625 | 688.39 | 11.405 | 1.8808 | 0.01504 | 394.0483 | 3397.7508 | 8622.6764 | 4994693.6094 | 12675334.3116 | 0.0013 | 0.7112 | 0.011405 | 0.68839 | 0.0001625 | 1025811.2986 | 700 | 1030 | 0.7 | 8.154 | 8.154 | 0 |  | Elevation Head Loss | 1000 | m
14 | 0.17396 | 688.7025 | 11.2487 | 1.8791 | 0.015205 | 397.4489 | 3427.0732 | 8622.6764 | 5037797.6474 | 12675334.3116 | 0.0013 | 0.7112 | 0.011249 | 0.6887 | 0.00017396 | 1025345.8348 | 700 | 1030 | 0.7 | 8.1099 | 8.1099 | 0 |  | Annual hours of operation | 8400 | h/yr
15 | 0.18542 | 689.015 | 11.0925 | 1.8774 | 0.015363 | 400.6917 | 3455.0344 | 8622.6764 | 5078900.6373 | 12675334.3116 | 0.0013 | 0.7112 | 0.011092 | 0.68902 | 0.00018542 | 1024880.7933 | 700 | 1030 | 0.7 | 8.0678 | 8.0678 | 0 |  | Pump Efficiency | 0.82 | %
16 | 0.19687 | 689.3275 | 10.9362 | 1.8757 | 0.015517 | 403.7884 | 3481.737 | 8622.6764 | 5118153.3229 | 12675334.3116 | 0.0013 | 0.7112 | 0.010936 | 0.68933 | 0.00019687 | 1024416.1735 | 700 | 1030 | 0.7 | 8.0277 | 8.0277 | 0 |  | Pump Power | 11491330.8749 | W
17 | 0.20833 | 689.64 | 10.78 | 1.874 | 0.015667 | 406.7498 | 3507.2715 | 8622.6764 | 5155689.0832 | 12675334.3116 | 0.0013 | 0.7112 | 0.01078 | 0.68964 | 0.00020833 | 1023951.9747 | 700 | 1030 | 0.7 | 7.9894 | 7.9894 | 0 |  | Energy cost | 0.175 | W
18 | 0.21979 | 689.9525 | 10.6237 | 1.8723 | 0.015812 | 409.585 | 3531.7188 | 8622.6764 | 5191626.5634 | 12675334.3116 | 0.0013 | 0.7112 | 0.010624 | 0.68995 | 0.00021979 | 1023488.1964 | 700 | 1030 | 0.7 | 7.9527 | 7.9527 | 0 |  | Annual cost of energy · C |  | $/yr
19 | 0.23125 | 690.265 | 10.4675 | 1.8706 | 0.015953 | 412.3025 | 3555.1509 | 8622.6764 | 5226071.8212 | 12675334.3116 | 0.0013 | 0.7112 | 0.010467 | 0.69027 | 0.00023125 | 1023024.838 | 700 | 1030 | 0.7 | 7.9174 | 7.9174 | 0
20 | 0.24271 | 690.5775 | 10.3112 | 1.8689 | 0.01609 | 414.9098 | 3577.6327 | 8622.6764 | 5259120.0919 | 12675334.3116 | 0.0013 | 0.7112 | 0.010311 | 0.69058 | 0.00024271 | 1022561.899 | 700 | 1030 | 0.7 | 7.8836 | 7.8836 | 0
21 | 0.25417 | 690.89 | 10.155 | 1.8672 | 0.016224 | 417.4136 | 3599.2226 | 8622.6764 | 5290857.2509 | 12675334.3116 | 0.0013 | 0.7112 | 0.010155 | 0.69089 | 0.00025417 | 1022099.3788 | 700 | 1030 | 0.7 | 7.851 | 7.851 | 0
22 | 0.26562 | 691.2025 | 9.9987 | 1.8655 | 0.016354 | 419.8202 | 3619.9735 | 8622.6764 | 5321361.0348 | 12675334.3116 | 0.0013 | 0.7112 | 0.0099987 | 0.6912 | 0.00026562 | 1021637.2768 | 700 | 1030 | 0.7 | 7.8197 | 7.8197 | 0
23 | 0.27708 | 691.515 | 9.8425 | 1.8638 | 0.016481 | 422.135 | 3639.9334 | 8622.6764 | 5350702.0665 | 12675334.3116 | 0.0013 | 0.7112 | 0.0098425 | 0.69152 | 0.00027708 | 1021175.5924 | 700 | 1030 | 0.7 | 7.7894 | 7.7894 | 0
24 | 0.28854 | 691.8275 | 9.6862 | 1.8621 | 0.016606 | 424.3631 | 3659.1461 | 8622.6764 | 5378944.7226 | 12675334.3116 | 0.0013 | 0.7112 | 0.0096862 | 0.69183 | 0.00028854 | 1020714.3252 | 700 | 1030 | 0.7 | 7.7601 | 7.7601 | 0 |  |  | 0.7
25 | 0.3 | 692.14 | 9.53 | 1.8605 | 0.016728 | 426.5093 | 3677.6516 | 8622.6764 | 5406147.8708 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 0.0003 | 1020253.4745 | 700 | 1030 | 0.7 | 7.7319 | 7.7319 | 0
[9 empty] | 42711319.2466 | 115054516.7907
Yr | Pipe roughness [ mm ] | Interior Diameter [ mm ] | Wall thickness [ mm ] | Fluid Velocity [m/s] | Friction factor f | Head Loss [ m ] | Pump Friction [ kW ] | Pump Elevation [ kW ] | Electricity Friction [ M$ ] | Electricity Elevation [ M$ ] | Viscosity [ Pa·s ] | Outside Diameter [m] | Wall thickness [m] | Inside Diameter [m] | Pipe roughness [m] | Reynolds Number Re | Flow [L/s] | Density kg/m3 | Flow Rate [m3/s] | Eq Left Side | Eq Right Side | f diff Error
1 | 0.015 | 692.14 | 9.53 | 1.8605 | 0.01208 | 308.0206 | 2655.9623 | 8622.6764 | 3904264.6308 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.5e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0983 | 9.0983 | 0
2 | 0.015833 | 692.14 | 9.53 | 1.8605 | 0.012105 | 308.6485 | 2661.376 | 8622.6764 | 3912222.6827 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.5833e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.089 | 9.089 | 0
3 | 0.016667 | 692.14 | 9.53 | 1.8605 | 0.01213 | 309.272 | 2666.7528 | 8622.6764 | 3920126.5902 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.6667e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0798 | 9.0798 | 0
4 | 0.0175 | 692.14 | 9.53 | 1.8605 | 0.012154 | 309.8914 | 2672.0933 | 8622.6764 | 3927977.2133 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.75e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0707 | 9.0707 | 0
5 | 0.018333 | 692.14 | 9.53 | 1.8605 | 0.012178 | 310.5066 | 2677.3982 | 8622.6764 | 3935775.3914 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.8333e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0618 | 9.0618 | 0
6 | 0.019167 | 692.14 | 9.53 | 1.8605 | 0.012202 | 311.1178 | 2682.668 | 8622.6764 | 3943521.9438 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 1.9167e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0529 | 9.0529 | 0
7 | 0.02 | 692.14 | 9.53 | 1.8605 | 0.012226 | 311.7249 | 2687.9032 | 8622.6764 | 3951217.6703 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.044 | 9.044 | 0
8 | 0.020833 | 692.14 | 9.53 | 1.8605 | 0.012249 | 312.3281 | 2693.1043 | 8622.6764 | 3958863.352 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.0833e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0353 | 9.0353 | 0
9 | 0.021667 | 692.14 | 9.53 | 1.8605 | 0.012273 | 312.9274 | 2698.2719 | 8622.6764 | 3966459.7517 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.1667e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0266 | 9.0266 | 0
10 | 0.0225 | 692.14 | 9.53 | 1.8605 | 0.012296 | 313.5229 | 2703.4065 | 8622.6764 | 3974007.6147 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.25e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0181 | 9.0181 | 0
11 | 0.023333 | 692.14 | 9.53 | 1.8605 | 0.012319 | 314.1146 | 2708.5086 | 8622.6764 | 3981507.669 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.3333e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0096 | 9.0096 | 0
12 | 0.024167 | 692.14 | 9.53 | 1.8605 | 0.012343 | 314.7026 | 2713.5787 | 8622.6764 | 3988960.6262 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.4167e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 9.0011 | 9.0011 | 0
13 | 0.025 | 692.14 | 9.53 | 1.8605 | 0.012365 | 315.2869 | 2718.6171 | 8622.6764 | 3996367.1816 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.5e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9928 | 8.9928 | 0
14 | 0.025833 | 692.14 | 9.53 | 1.8605 | 0.012388 | 315.8676 | 2723.6245 | 8622.6764 | 4003728.015 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.5833e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9845 | 8.9845 | 0
15 | 0.026667 | 692.14 | 9.53 | 1.8605 | 0.012411 | 316.4448 | 2728.6012 | 8622.6764 | 4011043.791 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.6667e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9763 | 8.9763 | 0
16 | 0.0275 | 692.14 | 9.53 | 1.8605 | 0.012433 | 317.0185 | 2733.5477 | 8622.6764 | 4018315.1595 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.75e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9682 | 8.9682 | 0
17 | 0.028333 | 692.14 | 9.53 | 1.8605 | 0.012456 | 317.5887 | 2738.4645 | 8622.6764 | 4025542.7562 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.8333e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9602 | 8.9602 | 0
18 | 0.029167 | 692.14 | 9.53 | 1.8605 | 0.012478 | 318.1555 | 2743.3518 | 8622.6764 | 4032727.2028 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 2.9167e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9522 | 8.9522 | 0
19 | 0.03 | 692.14 | 9.53 | 1.8605 | 0.0125 | 318.7189 | 2748.2103 | 8622.6764 | 4039869.1076 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9443 | 8.9443 | 0
20 | 0.030833 | 692.14 | 9.53 | 1.8605 | 0.012522 | 319.2791 | 2753.0402 | 8622.6764 | 4046969.0659 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.0833e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9364 | 8.9364 | 0
21 | 0.031667 | 692.14 | 9.53 | 1.8605 | 0.012544 | 319.836 | 2757.8419 | 8622.6764 | 4054027.6602 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.1667e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9286 | 8.9286 | 0
22 | 0.0325 | 692.14 | 9.53 | 1.8605 | 0.012566 | 320.3896 | 2762.616 | 8622.6764 | 4061045.4606 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.25e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9209 | 8.9209 | 0
23 | 0.033333 | 692.14 | 9.53 | 1.8605 | 0.012587 | 320.9401 | 2767.3626 | 8622.6764 | 4068023.0255 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.3333e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9132 | 8.9132 | 0
24 | 0.034167 | 692.14 | 9.53 | 1.8605 | 0.012609 | 321.4874 | 2772.0822 | 8622.6764 | 4074960.9011 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.4167e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.9057 | 8.9057 | 0
25 | 0.035 | 692.14 | 9.53 | 1.8605 | 0.01263 | 322.0317 | 2776.7753 | 8622.6764 | 4081859.6229 | 12675334.3116 | 0.0013 | 0.7112 | 0.00953 | 0.69214 | 3.5e-05 | 1020253.4745 | 700 | 1030 | 0.7 | 8.8981 | 8.8981 | 0
[9 empty] | 35957717.0794 | 115054516.7907

## Charts
[6 empty] | Sankey Diagrams |  |  |  | #REF! | #REF! | :Steel design #0a82b0
[6 empty] | https://sankeymatic.com/ |  | Steel design | Steel corrosion | #REF! | #REF! | :Steel #0a82b0 | #REF! | Coated [ 8.3 ] CAPEX
[6 empty] | Field Joint\nCoating [ 8.3 ] Coated\nCAPEX | 0 |  |  | Bare |  |  | #REF! | Coated [ 1.3 ] CAPEX
|  | Corrosion | Strategy |  |  | Shop Coating [ 1.3 ] Coated\nCAPEX | 0 |  |  | #REF! | #REF! | :Steel corrosion #0a82b0 | Bare [ 42.7 ] OPEX | Coated [ 36 ] OPEX
Type | Expenditure Category | Bare | Coated | Coated Savings |  | Coated\nFriction\nEnergy [ 36 ] Coated\nOPEX | 0 |  |  | #REF! | #REF! | :Dosing Plant #0a82b0 | Bare [ 10.2 ] OPEX | Coated [ 3.6 ] OPEX
CAPEX | Extra Steel for Corrosion | 5869704.947 | 0 | 5869704.947 |  | Coated\nInspections [ 3.6 ] Coated\nOPEX | 0 |  |  | Bare [ 42.7 ] OPEX | OPEX [ 42.7 ] Friction Energy | :Friction Energy #74b4dd | Bare [ 7.3 ] OPEX
CAPEX | Field Joint Coating | 0 | 8334000 | -8334000 | [5 empty] | Bare [ 10.2 ] OPEX | OPEX [ 10.2 ] Corrosion Inhibitors | :Inhibitors #74b4dd |  | CAPEX [ 8.3 ] Field Joint Coating
CAPEX | Shop-applied Coating | 0 | 1304653.1636 | -1304653.1636 |  | Coated\nCAPEX [ 8.3 ] Coated\nPipe | 0 |  |  | Bare [ 7.3 ] OPEX | OPEX [ 7.3 ] Inspections | :Inspections #74b4dd | #REF! | CAPEX [ 1.3 ] Shop-applied Coating
OPEX | Corrosion Inhibitors | 10223564.5737 | 0 | 10223564.5737 |  | Coated\nCAPEX [ 1.3 ] Coated\nPipe | 0 | [5 empty] | #REF! | OPEX [ 36 ] Friction Energy
OPEX | Friction Energy | 42711319.2466 | 35957717.0794 | 6753602.1672 |  | Coated\nOPEX [ 36 ] Coated\nPipe | 0 |  |  | Coated |  |  | OPEX [ 42.7 ] Friction Energy | OPEX [ 3.6 ] Inspections
OPEX | Inspections | 7261632.0146 | 3630816.0073 | 3630816.0073 |  | Coated\nOPEX [ 3.6 ] Coated\nPipe | 0 |  |  | Coated [ 8.3 ] CAPEX | CAPEX [ 8.3 ] Field Joint Coating | :Field Joint Coating #0a82b0 | OPEX [ 10.2 ] Corrosion Inhibitors
| Total CAPEX | 5869704.947 | 9638653.1636 | -3768948.2165 | 60.9% |  |  |  |  | Coated [ 1.3 ] CAPEX | CAPEX [ 1.3 ] Shop-applied Coating | :Shop Coating #0a82b0 | OPEX [ 7.3 ] Inspections | :Field Joint Coating #0a82b0
| Total OPEX | 60196515.8349 | 39588533.0867 | 20607982.7482 | [5 empty] | Coated [ 36 ] OPEX | OPEX [ 36 ] Friction Energy | :Friction Energy #74b4dd |  | :Shop Coating #0a82b0
| Total Expenditure | 66066220.782 | 49227186.2503 | 16839034.5317 | 25.49% | Coated\nPipe [ 49.2 ] Bare\nPipe | 0 |  |  | Coated [ 3.6 ] OPEX | OPEX [ 3.6 ] Inspections | :Inspections #74b4dd | :Steel corrosion #0a82b0 | :Friction Energy #74b4dd
[6 empty] | Savings [ 16.8 ] Bare\nPipe | 0 | [5 empty] | :Dosing Plant #0a82b0 | :Inspections #74b4dd
| Item | Bare Pipe | Coated Pipe | Difference | [8 empty] | :Friction Energy #74b4dd
| Extra Inhibitors | 10223564.5737 |  | 100% |  | Bare\nPipe [ 5.9 ] Bare\nCAPEX | 0 |  |  | 8.334 |  |  | :Inhibitors #74b4dd
| Extra Friction Energy | 6753602.1672 |  | 15.81% |  | Bare\nPipe [ 10.2 ] Bare\nOPEX | 0 |  |  | 1.3047 |  |  | :Inspections #74b4dd
| Extra Steel | 5869704.947 |  |  |  | Bare\nPipe [ 42.7 ] Bare\nOPEX | 0 |  |  | 9.6387
| Joint Field Coating |  | 8334000 | 100% |  | Bare\nPipe [ 7.3 ] Bare\nOPEX | 0
| Extra Inspections | 3630816.0073 |  | 50% | [5 empty] | 35.9577
| Shop Coating |  | 1304653.1636 | 100% | [5 empty] | 3.6308
[6 empty] | Bare\nCAPEX [ 5.9 ] Corrosion\nExtra Steel | 0 |  |  | 39.5885 | 49.2272
| Total | 26477687.6952 | 9638653.1636 | 16839034.5317 | 36.4% | Bare\nOPEX [ 42.7 ] Bare\nFriction\nEnergy | 0
|  |  | 0.5724 |  |  | Bare\nOPEX [ 10.2 ] Inhibitors | 0
[6 empty] | Bare\nOPEX [ 7.3 ] Bare\nInspections | 0
| Item | Bare | Coated
| Extra Inhibitors | 10.2236 |  |  |  | :Savings #0db14b | 0
| Extra Friction Energy | 6.7536 |  |  |  | :Coated\nPipe #00b5ff | 0
| Extra Steel | 5.8697 |  |  |  | :Bare\nPipe #005b80 | 0
| Joint Field Coating |  | 8.334 |  |  | :Bare\nCAPEX #003c54 | 0
| Extra Inspections | 3.6308 |  |  |  | :Bare\nOPEX #003c54 | 0
| Shop Coating |  | 1.3047 |  |  | :Coated\nCAPEX #009bd9 | 0
[6 empty] | :Coated\nOPEX #009bd9 | 0
[6 empty] | :Field Joint\nCoating #0080b3 | 0
[6 empty] | :Shop Coating #0080b3 | 0
[6 empty] | :Coated\nFriction\nEnergy #0080b3 | 0
[6 empty] | :Coated\nOPEX #0080b3 | 0
[6 empty] | :Coated\nInspections #0080b3 | 0

## SRAII AMSA
Instalación | psi | Ubicación Longitudinal (km) | Elevación (msnm) | Presión Operacional (kPa(g))
Túnel Las Ánimas | 1180.1742 | 0.47 | 1043.5 | 8137
Túnel La Guardia | 1132.3117 | 15.9 | 1031.4 | 7807
Túnel Coirón | 1314.4794 | 26 | 876.8 | 9063
Puente Estero Camisas | 1674.8988 | 12.7 | 666.5 | 11548
Puente Cruce Tranquilla | 1183.8002 | 40.8 | 923.7 | 8162
Puente Río Choapa | 1163.4948 | 42.1 | 933.9 | 8022
Instalación | max pressure | Ubicación Longitudinal (km) | Elevación (msnm) | Fuerza Máxima (kgf) | Máxima Presión Transiente (kPa(g))
Manifold 28" EB3 | 1444.8686 | 0 | 1020.5 | 23000 | 9962
Descarga Bombas 14" EB3 | 1307.8076 | 0 | 1020.5 | 9000 | 9017
Tunel Las Ánimas II 28" | 1444.8686 | 0.5 | 1043.5 | 23000 | 9962
Tunel La Guardia 28" | 1384.3877 | 15.9 | 1031.4 | 23000 | 9545
Túnel Coirón 28" | 1592.0821 | 26 | 876.5 | 20000 | 10977
Parámetro | Unidad | Valor
Temperatura Fluido | °C | 2024-10-25
Densidad Fluido | kg/m³ | 1000
Viscosidad Dinámica Fluido | cP | 1.3
Caudal de Diseño | m³/h | 2268
Velocidad Diseño | m/s | 1.584
Caudal Mínimo de operación | m³/h | 720
Rugosidad Absoluta Revestimiento Interior FBE | mm | 0.023
Velocidad Máxima de Operación Estaciones de Bombeo | m/s | 3
Velocidad Máxima de Operación Drenajes de Emergencia | m/s | 8

## Chilean_Projects
Name | Year | Owner | Size | Length | Strategy | Fluid | Constructor | Reparaciones | FBE | Cañerías | Revestidor | Tipo | Eng | Column1 | Que tal?
Monturaqui | 1998 | MEL | 36" | 90 | FBE | well | Techint | FBE | 3M |  |  | Weld |  |  | ✅✅✅ | - TE - Pendiente. Generado. Pendiente. 13º. - LE - Compacto. Mas pendiente. - Primer siempre es mejor. Fenolic. Base agua. | - FBE Socotrem.
Pelambres | 2007 | AMSA | 32 | 50 | FBE | recovered | Techint |  | solo uniones Tyhoo |  |  | Weld |  |  | 🟢🟠🟡
Coloso | 2008 | MEL | 24" | 130 | LE➜Bare | desal | Techint |  |  |  |  | Weld | Fluor |  | 🔴🟠🟡
Centinela | 2011 | AMSA | 36" | 160 | Bare | seawater | Techint |  |  |  |  | Weld
Candelaria | 2012 | Lundin | 24” | 80 | FBE&HDPE | desal | Techint |  | 3M |  |  | Weld
Cerro Negro | 2013 | CAP | 24 | 90 | FBE➜HDPE | desal | [5 empty] | Weld | Brass |  | 🔴🟠🟡
Mantoverde | 2013 | Capstone | 24" | 50 | FBE | desal | Techint |  |  |  |  | Weld
SGorda | 2014 | SGSCM | 36" | 140 | Bare➜HDPE | seawater | Techint |  |  |  |  | Weld |  |  | 🟢🟢🟢
EWS | 2014 | MEL | 2x42" | 160 | Primed FBE | desal | Techint |  | 3M | Jindal | AQahtani | Weld | Bechtel | SaudiAramco | 🟡🟢🟢 | - CPRS. 5meses de atrasos. Double joint. Lanza. | - Inspecciones - Zonas altas: Punto de rocia caía tanto enla noche. Cura en funcion de la tempratura. Dew point caía tanto que. Viscocidad baja.
Spence SGO | 2018 | BHP | 36" | 160 | LE | desal |  |  | - | Jindal | Jindal | Weld | Brass
EWSE | 2019 | MEL | 2x42" | 160 | Primed FBE | desal | Techint
INCO | 2022 | AMSA | 24" | 60 | Bare | desal | Techint |  |  | Jindal |  | Weld/Vic | ProPipe |  | 🟡🟢🟢
QBlanca | 2023 | Teck | 36" | 160 | Bare | desal | Techint |  |  |  |  | Weld | Ausenco
Aconcagua | 2025 | APacifico | 28" | 120 | LE | desal | [5 empty] | Weld | BIOS
PAO | 2026 | AMSA | 28" | 60 | Primed FBE | desal | Techint |  | KCC | MAceros | Tyhoo | Weld | Fluor
C20+ | 2026 | CMDIC | 44" | 194 | FBE | desal | Techint |  | 3M | Corinth Pipeworks | AQahtani | Weld | Bechtel
RTomic | 2026 | Codelco | 48" | 160 | LE | desal | Techint |  | HPadur | Jindal | Jindal | Weld
Capellan | 2026 | Adasa | 28" | 24 | Bare | recovered | [5 empty] | Weld | Ifarle
TEA | 2026 | SQM | 36" | 90 | FBE | seawater
Cenizas | 2027 | MCenizas | 12" | 120 | FBE | desal | [5 empty] | Weld | BIOS
SDomingo | 2026 | SDomingo
Algorta | 2021 | AlgortaN | 18" | 70 | GRP | seawater | Techint |  |  |  |  | Weld | Bechtel |  | 🔴🟠🟡🩹
Los Bronces | 2009 | AngloAm | 20-24" | 60 | ?? | recovered | Techint | [7 empty] | 🟢🟠🟡
Algorta | 2021 | AlgortaN | 18" | 20 | HDPE | seawater | [5 empty] | Weld | Bechtel |  | 🟡🟢🟢
Coloso | 2008 | MEL | 24" | 20 | LE➜HDPE | desal | Techint |  |  |  |  | Weld | Fluor |  | 🔴🟠🟡
Quellaveco | 2018 | AngloAm | 28" | 30 | P FBE➜HDPE | river | Techint |  | 3M | Jindal | Jindal | Weld | Fluor |  | 🟢🟢🟢
Quellaveco | 2018 | AngloAm | 30" | 30 | PU | recovered | Techint |  | Protegol | Jindal |  | Weld | Fluor |  | 🔴🟠🟡🩹