## FBE or not to FBE
Pipeline Main Variables | [8 empty] | 0.003125
Name | variable | units | Name | variable | units | FBE Coated Case
Pipeline lenght | 70 | km |  |  |  | Year | Inner diameter | Flow vel | Roughness factor | Solve for f | Reinlods Num | Friction Factor | f with Colebrook-White Equation | Friction Head Loss | Pump Total Power | OPEX | Dif OPEX |  | Inner Diameter
Pipeline lenght | 70000 | m | Steel cost including transportation | 1295 | US$/MT | 1 | 0.69214 | 1.8605 | 0.005 | 0.10943 | 1020253.4745 | 0.011518 | 0.01175 | 205.5003 | 10398.1901 | 9356574.2944 | 494651.1796 | 0.00023206 | 692.14
Design flow rate | 700 | L/s | Electrical energy cost | 0.107 | US$/kWh | 2 | 0.69214 | 1.8605 | 0.008125 | 0.10618 | 1020253.4745 | 0.011621 | 0.011859 | 207.3406 | 10414.0632 | 9370857.3317 | 496244.5798 | 0.00023766 | 692.14
Design flow rate | 0.7 | m³/s |  |  |  | 3 | 0.69214 | 1.8605 | 0.01125 | 0.0976 | 1020253.4745 | 0.011734 | 0.011964 | 209.3622 | 10431.5011 | 9386548.4569 | 495597.7932 | 0.00022945 | 692.14
Design flow rate | 2520 | m³/h |  |  |  | 4 | 0.69214 | 1.8605 | 0.014375 | 0.089935 | 1020253.4745 | 0.011843 | 0.012065 | 211.312 | 10448.3195 | 9401682.056 | 494712.4404 | 0.0002219 | 692.14
Static Head (elevation change) | 1000 | m | Density of water | 1030 | kg/m³ | 5 | 0.69214 | 1.8605 | 0.0175 | 0.083058 | 1020253.4745 | 0.011949 | 0.012164 | 213.1959 | 10464.5695 | 9416304.2343 | 493293.1239 | 0.00021493 | 692.14
Pipeline Outside diameter | 28 | inches | Dynamic Viscosity of water | 1.3 | cP | 6 | 0.69214 | 1.8605 | 0.020625 | 0.076862 | 1020253.4745 | 0.012051 | 0.01226 | 215.0192 | 10480.2959 | 9430455.3595 | 492136.0989 | 0.00020847 | 692.14
Pipeline Outside diameter | 711.2 | mm | Kinematic viscosity of water | 1.2621e-06 | m²/s | 7 | 0.69214 | 1.8605 | 0.02375 | 0.07126 | 1020253.4745 | 0.01215 | 0.012353 | 216.7863 | 10495.5385 | 9444170.994 | 490455.9391 | 0.00020247 | 692.14
Pipeline Outside diameter | 0.7112 | m | Kinematic viscosity of water | 1.2621 | cSt | 8 | 0.69214 | 1.8605 | 0.026875 | 0.066176 | 1020253.4745 | 0.012246 | 0.012443 | 218.5014 | 10510.332 | 9457482.6428 | 488852.0674 | 0.00019688 | 692.14
Service life | 25 | years | Annual hours of pump operation | 8409.6 | h/yr | 9 | 0.69214 | 1.8605 | 0.03 | 0.061548 | 1020253.4745 | 0.01234 | 0.012531 | 220.168 | 10524.7078 | 9470418.3599 | 487043.4995 | 0.00019166 | 692.14
Safety Factor | 1.15 |  | API 5L X70 · Steel density | 7850 | kg/m³ | 10 | 0.69214 | 1.8605 | 0.033125 | 0.057322 | 1020253.4745 | 0.012431 | 0.012617 | 221.7894 | 10538.6937 | 9483003.2446 | 485041.5479 | 0.00018676 | 692.14
Supply contingency | 0% |  | Gravitational acceleration | 9.81 | m/s² | 11 | 0.69214 | 1.8605 | 0.03625 | 0.07065 | 1020253.4745 | 0.012474 | 0.012701 | 222.5591 | 10545.3325 | 9488977.0518 | 489139.3819 | 0.00022753 | 692.14
Pipe segment length | 12 | m |  |  |  | 12 | 0.69214 | 1.8605 | 0.039375 | 0.049899 | 1020253.4745 | 0.012605 | 0.012783 | 224.908 | 10565.5936 | 9507208.5236 | 480498.1434 | 0.00017783 | 692.14 | [11 empty] | 0.7
FBE thickness | 0.3 | mm | Pump efficiency | 82% |  | 13 | 0.69214 | 1.8605 | 0.0425 | 0.046629 | 1020253.4745 | 0.01269 | 0.012863 | 226.4102 | 10578.5507 | 9518867.6907 | 477975.0216 | 0.00017375 | 692.14
FBE repair robot cost per joint | 1150 | US$/joint | Tasa descuento anual para cálculo VAN | 10% |  | 14 | 0.69214 | 1.8605 | 0.045625 | 0.043613 | 1020253.4745 | 0.012772 | 0.012942 | 227.8772 | 10591.2047 | 9530254.0949 | 475295.3491 | 0.00016989 | 692.14
Welding cost per joint | [5 empty] | 15 | 0.69214 | 1.8605 | 0.04875 | 0.040824 | 1020253.4745 | 0.012852 | 0.013018 | 229.3111 | 10603.5726 | 9541383.0001 | 472466.6624 | 0.00016624 | 692.14
Wall thickness corrosion rate | 0.2 | mm/yr |  |  |  | 16 | 0.69214 | 1.8605 | 0.051875 | 0.038241 | 1020253.4745 | 0.012931 | 0.013094 | 230.7135 | 10615.6697 | 9552268.3641 | 469495.9634 | 0.00016278 | 692.14 |  |  | Difference
|  |  | Wall thickness. No corrosion. | 9.53 | mm | 17 | 0.69214 | 1.8605 | 0.055 | 0.035843 | 1020253.4745 | 0.013008 | 0.013167 | 232.0863 | 10627.5105 | 9562922.9859 | 466389.7718 | 0.00015949 | 692.14 |  |  | Bare | FBE | Units
Roughness factor bare pipe year 1 | 0.1 | mm | Roughness factor FBE coated pipe year 1 | 0.02 | mm | 18 | 0.69214 | 1.8605 | 0.058125 | 0.033613 | 1020253.4745 | 0.013083 | 0.01324 | 233.4308 | 10639.1079 | 9573358.6338 | 463154.1709 | 0.00015636 | 692.14 | OPEX | Small ID & Roughness Extra Energy | #REF! |  | MUS$/yr
Roughness factor bare pipe year 25 | 0.3 | mm | Roughness factor FBE coated pipe year 25 | 0.02 | mm | 19 | 0.69214 | 1.8605 | 0.06125 | 0.031536 | 1020253.4745 | 0.013157 | 0.01331 | 234.7485 | 10650.474 | 9583586.1549 | 459794.8483 | 0.00015338 | 692.14 |  | Corrosion Inhibitors | #REF! |  | MUS$/yr
[6 empty] | 20 | 0.69214 | 1.8605 | 0.064375 | 0.029599 | 1020253.4745 | 0.013229 | 0.01338 | 236.0407 | 10661.6199 | 9593615.5713 | 456317.1312 | 0.00015053 | 692.14 |  | Annual expenses | #REF! |  | MUS$/yr
[6 empty] | 21 | 0.69214 | 1.8605 | 0.0675 | 0.027788 | 1020253.4745 | 0.0133 | 0.013448 | 237.3086 | 10672.556 | 9603456.1633 | 452726.0187 | 0.00014782 | 692.14
[6 empty] | 22 | 0.69214 | 1.8605 | 0.070625 | 0.026094 | 1020253.4745 | 0.01337 | 0.013515 | 238.5532 | 10683.2918 | 9613116.5421 | 449026.2093 | 0.00014522 | 692.14 | CAPEX | Present value annual expenses | #REF! |  | MUS$ |  | 400 | $/L/s
[6 empty] | 23 | 0.69214 | 1.8605 | 0.07375 | 0.024506 | 1020253.4745 | 0.013439 | 0.013582 | 239.7757 | 10693.8362 | 9622604.7146 | 445222.1266 | 0.00014274 | 692.14 |  | FBE repair robot |  | 6708333.3333 | MUS$ | PASIVAN 550 | 28170 | 70.425 | Corrosion inhibitor through passivation | 70 | 28000
[6 empty] | 24 | 0.69214 | 1.8605 | 0.076875 | 0.023016 | 1020253.4745 | 0.013506 | 0.013646 | 240.9769 | 10704.1976 | 9631928.1392 | 441317.9413 | 0.00014035 | 692.14 |  | Extra Steel | #REF! |  | MUS$ | BC 130 | 3686 | 9.215 | Deoxygenation Agents | 50 | 21000
[6 empty] | 25 | 0.69214 | 1.8605 | 0.08 | 0.046207 | 1020253.4745 | 0.013498 | 0.01371 | 240.8302 | 10702.932 | 9630789.3716 | 447298.8657 | 0.00021248 | 692.14 |  | FBE inner coating |  | #NAME? | MUS$ | Servicio de aplicación y control | 7210 | 18.025 | Biocide | 9 | 3600
[21 empty] | Total | #REF! |  | MUS$ |  |  |  | pH Adjusters | 3 | 1200
[6 empty] | Bare Pipe Case | [19 empty] | 39466 |  | Energy Cost | 5 | 2000
[6 empty] | Year | Inner diameter | Flow vel | Roughness factor | Solve for f | Reinlods Num | Friction Factor | f with CBrook-W | Friction Head Loss | Pump Total Power | OPEX | 7.7779e-07 |  | Inner Diameter | [8 empty] | Application and QA service | 18 | 7200
CAPEX · Cost of Steel · Bare Pipe | [5 empty] | 1 | 0.68214 | 1.9154 | 0.1 | -8.1051e-05 | 1035210.1325 | 0.014031 | 0.014021 | 269.2312 | 10947.9081 | 9851225.474 | 8.9e-05 |  | 682.14 | [9 empty] | 155 | 62000
W | 249.6389 | kg/m |  |  |  | 2 | 0.68256 | 1.9131 | 0.10833 | -1.4862e-05 | 1034578.1886 | 0.01418 | 0.014174 | 271.2767 | 10965.552 | 9867101.9115 | 8.9e-05 |  | 682.5567
W total | 17474722.7117 | kg |  |  |  | 3 | 0.68297 | 1.9107 | 0.11667 | -1.0823e-05 | 1033947.0157 | 0.014325 | 0.01432 | 273.215 | 10982.2711 | 9882146.2501 | 8.9e-05 |  | 682.9733
CAPEX · Cost of Steel · Bare Pipe | [5 empty] | 4 | 0.68339 | 1.9084 | 0.125 | -7.3798e-06 | 1033316.6125 | 0.014466 | 0.014462 | 275.0507 | 10998.1055 | 9896394.4964 | 8.9e-05 |  | 683.39
W | 164.9094 | kg/m |  |  |  | 5 | 0.68381 | 1.9061 | 0.13333 | 0.00060444 | 1032686.9775 | 0.0146 | 0.0146 | 276.7518 | 11012.7782 | 9909597.3582 | 8.9e-05 |  | 683.8067
W total | 11543656.0627 | kg |  |  |  | 6 | 0.68422 | 1.9038 | 0.14167 | 0.00026546 | 1032058.1094 | 0.014733 | 0.014733 | 278.4259 | 11027.2188 | 9922591.4584 | 8.9e-05 |  | 684.2233 |  |  |  | 28170
[6 empty] | 7 | 0.68464 | 1.9014 | 0.15 | 0.0005502 | 1031430.0067 | 0.01486 | 0.01486 | 279.9766 | 11040.5942 | 9934626.9331 | 0 |  | 684.64 |  |  |  | 3686
[6 empty] | 8 | 0.68506 | 1.8991 | 0.15833 | 0.00030828 | 1030802.6681 | 0.014986 | 0.014986 | 281.485 | 11053.6053 | 9946334.7102 | 0 |  | 685.0567
[6 empty] | 9 | 0.68547 | 1.8968 | 0.16667 | 0.0001069 | 1030176.0922 | 0.015108 | 0.015108 | 282.9186 | 11065.9712 | 9957461.8595 | 0 |  | 685.4733 |  | #REF!
[6 empty] | 10 | 0.68589 | 1.8945 | 0.175 | -6.0235e-05 | 1029550.2775 | 0.015227 | 0.015227 | 284.2821 | 11077.7322 | 9968044.7925 | 0 |  | 685.89
[6 empty] | 11 | 0.68631 | 1.8922 | 0.18333 | -0.0001983 | 1028925.2227 | 0.015343 | 0.015343 | 285.5798 | 11088.9251 | 9978116.4337 | 0 |  | 686.3067
[6 empty] | 12 | 0.68672 | 1.8899 | 0.19167 | -0.00031163 | 1028300.9263 | 0.015456 | 0.015456 | 286.8154 | 11099.583 | 9987706.667 | 0 |  | 686.7233
[6 empty] | 13 | 0.68714 | 1.8876 | 0.2 | -0.00040382 | 1027677.3872 | 0.015567 | 0.015567 | 287.9925 | 11109.7361 | 9996842.7123 | 0 |  | 687.14 |  | #REF!
[6 empty] | 14 | 0.68756 | 1.8853 | 0.20833 | -0.00047792 | 1027054.6037 | 0.015675 | 0.015675 | 289.1142 | 11119.4121 | 10005549.444 | 0 |  | 687.5567
[6 empty] | 15 | 0.68797 | 1.8831 | 0.21667 | -0.0005365 | 1026432.5746 | 0.01578 | 0.01578 | 290.1836 | 11128.6363 | 10013849.6625 | 0 |  | 687.9733 |  | #NAME?
[6 empty] | 16 | 0.68839 | 1.8808 | 0.225 | -0.00058172 | 1025811.2986 | 0.015884 | 0.015884 | 291.2034 | 11137.4321 | 10021764.3275 | 0 |  | 688.39
[6 empty] | 17 | 0.68881 | 1.8785 | 0.23333 | -0.00061544 | 1025190.7741 | 0.015985 | 0.015985 | 292.1759 | 11145.8208 | 10029312.7577 | 0 |  | 688.8067
[6 empty] | 18 | 0.68922 | 1.8762 | 0.24167 | -0.00063924 | 1024570.9999 | 0.016084 | 0.016084 | 293.1036 | 11153.8224 | 10036512.8047 | 0 |  | 689.2233
[6 empty] | 19 | 0.68964 | 1.874 | 0.25 | -0.00065447 | 1023951.9747 | 0.016182 | 0.016182 | 293.9885 | 11161.4552 | 10043381.0032 | 0 |  | 689.64
[6 empty] | 20 | 0.69006 | 1.8717 | 0.25833 | -0.0006623 | 1023333.697 | 0.016277 | 0.016277 | 294.8326 | 11168.7363 | 10049932.7026 | 0 |  | 690.0567
[6 empty] | 21 | 0.69047 | 1.8695 | 0.26667 | -0.00066372 | 1022716.1654 | 0.016371 | 0.016371 | 295.6378 | 11175.6815 | 10056182.182 | 0 |  | 690.4733
[6 empty] | 22 | 0.69089 | 1.8672 | 0.275 | -0.00065961 | 1022099.3788 | 0.016463 | 0.016463 | 296.4057 | 11182.3056 | 10062142.7514 | 0 |  | 690.89
[6 empty] | 23 | 0.69131 | 1.8649 | 0.28333 | -0.00065071 | 1021483.3356 | 0.016554 | 0.016554 | 297.1381 | 11188.6225 | 10067826.8412 | 0 |  | 691.3067
[6 empty] | 24 | 0.69172 | 1.8627 | 0.29167 | -0.00063769 | 1020868.0346 | 0.016643 | 0.016643 | 297.8363 | 11194.645 | 10073246.0806 | 0 |  | 691.7233
[6 empty] | 25 | 0.69214 | 1.8605 | 0.3 | -7.3432e-05 | 1020253.4745 | 0.016728 | 0.01673 | 298.4601 | 11200.0262 | 10078088.2372 | 2.3334e-06 |  | 692.14
[7 empty] | 0.00041667 |  | 0.0083333